## Bowtie Elements
Element ID | Element Type | Parent ID | System | Title | Description | Barrier Category | Barrier Owner | Barrier Condition | PFD | SIL | Provenance | Provenance Detail | Consequence Cat. | Severity | Gap Flag
HAZ-N-001 | HAZARD |  | Node 1 | Fluid in Node 1 | Fluid: fluid Location: Node 1
TE-N-001 | TOP_EVENT | HAZ-N-001 | Node 1 | Loss of containment of fluid from Node 1 | Loss of containment of fluid from Node 1
THR-N-001 | THREAT | TE-N-001 | Node 1 | Instrumentation or control system failure | Instrumentation or control system failure
PB-N-001 | PREVENTION | THR-N-001 | Node 1 | PSV: PSV set (Safeguard 3: relief valve sized for fire case) | PSV: PSV set (Safeguard 3: relief valve sized for fire case) | Hardware - Passive | MI Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 4 S=5.
CON-N-001 | CONSEQUENCE | TE-N-001 | Node 1 | Consequence 3: overpressure leading to rupture | Consequence 3: overpressure leading to rupture | [7 empty] | E | 5

## Threat-Consequence Links
Link ID | System | Threat ID | Threat Title | Consequence ID | Consequence Title | Severity
L--N-001-01 | Node 1 | THR-N-001 | Instrumentation or control system failure | CON-N-001 | Consequence 3: overpressure leading to rupture | 5

## Gap Analysis
Finding ID | Priority | System | Gap Type | Affected Pathway | Current State | Required State | Recommendation | Action Owner | Target
F-001 | CRITICAL | Node 1 | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 0 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-002 | CRITICAL | Node 1 | Missing mitigation barriers | PB-N-001 | Single barrier on instrumentation_failure pathway (THR-N-001). Single point of failure on S=5 catastrophic consequence. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-SCOPE-001 | CRITICAL | Cross-cutting (all systems) | Incomplete asset-level HAZOP coverage | All pathways | Submitted HAZOP covers 0 of 32 mandatory systems for CCGT scope (0%). Classification: LIMITED. | Complete Combined Cycle Gas Turbine asset-level HAZOP coverage per Ascendera Thermal Power Reference Scope v1.0, with all 32 mandatory systems for this variant covered by HAZOP deviations, causes, consequences, and safeguards. Reference: IEC 61882:2016 Cl. 5.3.3, IFC Performance Standards, IFC EHS Thermal Power 2008, NFPA 850 for electric generating stations, and variant-specific standards from the reference scope. | Extend HAZOP scope to cover the missing mandatory systems: Fuel Gas Receiving Station, Fuel Gas Heating, Filtration and Let-down, Gas Turbine and Enclosure, Gas Turbine Fuel Manifold, Nozzles, Purge, Gas Turbine Lubrication System, GT Enclosure Ventilation and Fire Suppression, HRSG Drums (HP/IP/LP) and Downcomer System, Superheater and Reheater, Economiser, Steam Turbine, Steam Turbine Lube, Seal, and Control Oil, Condenser (Surface or Air-Cooled), Condensate Polishing, Feedwater System (HP / IP / LP), Demineralisation Water Treatment, Boiler Water Chemical Dosing, Auxiliary (Closed-Loop) Cooling Water System, Generator, Exciter, Cooling, Seal Oil, Generator Step-Up Transformer, Unit Auxiliary and Station Service Transformers, HV / EHV Switchyard (AIS or GIS), Medium Voltage Switchgear, Emergency Diesel Generator, Distributed Control System and SCADA, Safety Instrumented System / Emergency Shutdown, Fire and Gas Detection, Plant Fire Water System, Special Hazard Fire Suppression, Instrument Air Compression, Drying, Distribution, Plant Service Air, Nitrogen Generation and Distribution, HVAC for MCC, Chemical Buildings, Control Room. | Process Safety Lead | 60 days
F-SYS-001 | MAJOR | Cross-cutting (all systems) | HAZOP methodology gap | All pathways | HAZOP methodology gap: the source HAZOP safeguard set is dominated by instrumented hardware barriers (alarms, trips, interlocks, valve position feedback). Of 0 human / procedural / organizational barriers in this assessment only 0 were extracted from HAZOP rows; the rest were added from domain knowledge and engineering standards. Emergency operating procedures, permit-to-work systems, pre-startup safety reviews, shift handover protocols, and management-of-change processes are not documented as HAZOP safeguards. Recommendation: run a supplementary workshop focused on non-hardware barriers so they are captured as HAZOP safeguards rather than tool inferences. Owner: Process Safety Lead. Target: 90 days. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Add human / procedural barriers (emergency procedures, permit-to-work, competency requirements) to the HAZOP. | Facility Owner | 90 days
F-SYS-002 | MAJOR | Cross-cutting (all systems) | Defence-in-depth diversity gap | All pathways | Defence-in-depth diversity gap: barrier type distribution across the assessment is Hardware-Active 0%, Hardware-Passive 100%, Procedural 0%, Organizational 0%, Human-Active 0%. Barrier ownership is concentrated: MI Eng owns 100% of all barriers; Operations owns 0%. Per CCPS / EI each critical threat pathway should have barriers from at least two of three categories (Technical / Operational / Organizational). Conduct a barrier-diversity review with multi-discipline participation (Operations, Maintenance, HSE, I&C). Owner: HSSE Manager. Target: 90 days. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Run a multi-discipline barrier-diversity review so each pathway has both technical and operational defences. | Facility Owner | 90 days
F-SYS-003 | MAJOR | Cross-cutting (all systems) | Critical barrier effectiveness concern | All pathways | Critically low barrier effectiveness on high-severity systems: Node 1 (0% Effective at S=5). Partially Effective barriers cannot be credited at full PFD value in a LOPA -- typical practice is to inflate the failure probability by 2-10x. On systems with Maximum Credible Consequence of S>=4 this represents a genuine residual-risk concern, not a desk-review artefact. Phase 2 site verification must resolve each barrier's condition to Effective or identify the required improvement. Owner: Mechanical Integrity Engineer. Target: 90 days. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Complete site verification of barrier condition on the high-severity systems listed; upgrade any barrier that cannot be confirmed Effective. | Facility Owner | 90 days
F-003 | MAJOR | Node 1 | Common-cause failure vulnerability | All pathways | Common-cause failure vulnerability on Node 1: 100% of barriers (1/1) are owned by MI Eng. A systematic failure in that discipline's domain (DCS failure, instrument air loss, staffing gap) would simultaneously degrade the majority of barriers. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Assess common-cause failure modes for MI Eng-owned barriers on Node 1. Consider diversifying barrier ownership by adding operational or procedural layers. | Facility Owner | 90 days
F-SCOPE-002 | MAJOR | Cross-cutting (all systems) | Variant not declared for thermal power scope | All pathways | Variant not declared on CLI; scope benchmark defaulted to natural gas CCGT. A hydrogen-ready, cogeneration, coal, biomass, waste-to-energy, or reciprocating plant has materially different mandatory scope and cannot be assessed accurately against the default. | Variant explicitly declared via --variant {ccgt¦ocgt¦cogen¦ccgt_h2¦pc¦cfb¦oil¦biomass¦efw¦recip} so the mandatory-system benchmark matches the plant architecture. | Re-run the pipeline with --variant set to the plant's actual technology variant, then review the updated scope completeness report. | Facility Owner | 90 days

## SCE Register
SCE ID | Type | System | Barrier ID | Barrier Title | Side | Associated MAH | Consequence Cat. | Functionality | Availability | Reliability | Survivability | Test Interval | Owner
SCE-001 | SCE | Node 1 | PB-N-001 | PSV: PSV set (Safeguard 3: relief valve sized for fire case) | Prevention | MAH-001 | E | PSV: PSV set (Safeguard 3: relief valve sized for fire case): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 12 months bench test / 60 months overhaul | MI Eng

## Summary
qassim_sample.xlsx -- Bowtie Risk Assessment Training Data
Evidence confidence cap: 65/100 (desk review) ¦ Structural confidence: 85%
Facility
Facility name | qassim_sample.xlsx
Technology | CCGT
Source file | /data/output/4d9cf73c-9686-4497-96ab-51c8bc4485e4/input.xlsx
Generated | 2026-04-26T19:07:14+00:00
Dataset Metrics
Bowtie systems | 1
Total elements | 5
Threats | 1
Consequences | 1
Prevention barriers | 1
Mitigation barriers | 0
Total barriers | 1
Gap findings (total) | 8
CRITICAL | 3
MAJOR | 5
MINOR | 0
SCE | 1
SCA | 0
Barrier Provenance Breakdown
Tier | Count | Definition
From HAZOP | 1 | Row-level verified with instrument tags
From HAZOP (limited) | 0 | Traceable but sparse HAZOP support
Aggregated from HAZOP | 0 | Synthesised from multiple HAZOP rows
Derived from HAZOP | 0 | Logically inferred from HAZOP data
Engineering standard | 0 | Based on industry code / standard
Domain knowledge | 0 | Expert knowledge (HAZOP gap)
Suggested | 0 | Gap-fill requiring site validation
System Summary
System | Threats | Consequences | Prevention | Mitigation | Gaps
Node 1 | 1 | 1 | 1 | 0 | 2
Known Limitations
1. Desk-review evidence cap 65/100 (non-negotiable).
2. PFD and SIL values require site validation; defaults seeded from catalogue.
3. Suggested barriers (blue rows) are gap-fill candidates.
4. FARSI performance standards are templates; site refinement required.

## HAZOP Source Map
Bowtie System | HAZOP Node(s) | HAZOP Node Name | Rows | S>=3 Scenarios | Notes
Node 1 | Node 1 | Node 1 | 200 | 120 | Full coverage; 80 row(s) below S>=3 threshold excluded.
(excluded) |  | Node 1 | 80 | 0 | No S>=3 rows / covered by parent system

## Audit Log
Element ID | Finding | Severity | Original | Corrected | Rationale
PB-N-001 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules