## Bowtie Elements
Element ID | Element Type | Parent ID | System | Title | Description | Barrier Category | Barrier Owner | Barrier Condition | PFD | SIL | Provenance | Provenance Detail | Consequence Cat. | Severity | Gap Flag
HAZ-AC-001 | HAZARD |  | ACC | Air cooled condenser | Condenser tube bundles (Vacuum, Ambient + 20 deg C) Fluid: Steam / condensate Location: ACC
TE-AC-001 | TOP_EVENT | HAZ-AC-001 | ACC | Loss of containment from air-cooled condenser | Loss of containment from air-cooled condenser
THR-AC-001 | THREAT | TE-AC-001 | ACC | Tube leak from corrosion or mechanical damage | 7. Electrical/Mechanical malfunctioning of drains pump 10LCB51-AP001/10LCB52-AP001.
PB-AC-019 | PREVENTION | THR-AC-001 | ACC | ACC is designed for worst case scenario including opening of LP/IP bypass. | ACC is designed for worst case scenario including opening of LP/IP bypass. | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3634 S=4.
PB-AC-018 | PREVENTION | THR-AC-001 | ACC | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2) | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3623 FAL-10LCA04-CF101A/B S=4. Also protects Condensate (FAL-10LCA04-CF101A/B).
PB-AC-017 | PREVENTION | THR-AC-001 | ACC | MOV-10MAJ45-AA075: Motor operated isolation valve | MOV-10MAJ45-AA075: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3612 MOV-10MAJ45-AA075 S=4.
PB-AC-016 | PREVENTION | THR-AC-001 | ACC | MOV-10LBG45-AA080: Motor operated isolation valve | MOV-10LBG45-AA080: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3606 MOV-10LBG45-AA080 S=4. Also protects Auxiliary Steam (MOV-10LBG45-AA080).
PB-AC-015 | PREVENTION | THR-AC-001 | ACC | PAL-10LBG45-CP001: Pressure alarm low (alert the operator) | PAL-10LBG45-CP001: Pressure alarm low (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3595 PAL-10LBG45-CP001 S=4. Also protects Auxiliary Steam (PAL-10LBG45-CP001).
PB-AC-014 | PREVENTION | THR-AC-001 | ACC | TAH-10MAJ42-CT122: Temperature alarm high (alert the operator) | TAH-10MAJ42-CT122: Temperature alarm high (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3578 TAH-10MAJ42-CT122 S=4.
THR-AC-002 | THREAT | TE-AC-001 | ACC | Vacuum system failure causing air ingress | 3. Malfunctioning and closure of MOV 10MAJ45-AA080 on common air take-off line.
MB-AC-001 | MITIGATION | TE-AC-001 | ACC | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-AC-003 | MITIGATION | TE-AC-001 | ACC | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-AC-004 | MITIGATION | TE-AC-001 | ACC | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-AC-002 | MITIGATION | TE-AC-001 | ACC | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-AC-001 | CONSEQUENCE | TE-AC-001 | ACC | Steam release / scald near walkway | Steam release / scald near walkway | [7 empty] | A | 3
MB-AC-005 | MITIGATION | CON-AC-001 | ACC | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-AC-002 | CONSEQUENCE | TE-AC-001 | ACC | Steam release causing equipment damage | Steam release causing equipment damage | [7 empty] | D | 4
HAZ-AX-001 | HAZARD |  | Auxiliary Steam | Auxiliary steam system for deaerator and tracing | Auxiliary steam header (8-14 bar, 180-220 deg C) Fluid: Auxiliary steam Location: Auxiliary Steam
TE-AX-001 | TOP_EVENT | HAZ-AX-001 | Auxiliary Steam | Loss of containment of auxiliary steam | Loss of containment of auxiliary steam
THR-AX-001 | THREAT | TE-AX-001 | Auxiliary Steam | Aux steam line leak at flanged connection | 1. Incorrect dosing of chemicals to BFW / Steam drum / DM water quality, etc.
PB-AX-004 | PREVENTION | THR-AX-001 | Auxiliary Steam | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 332 S=4.
PB-AX-003 | PREVENTION | THR-AX-001 | Auxiliary Steam | VALVE-10LBG10-AA406: Valve position feedback | VALVE-10LBG10-AA406: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 302 VALVE-10LBG10-AA406 S=4.
PB-AX-002 | PREVENTION | THR-AX-001 | Auxiliary Steam | VALVE-10LBC10-AA406: Valve position feedback | VALVE-10LBC10-AA406: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 298 VALVE-10LBC10-AA406 S=4.
PB-AX-001 | PREVENTION | THR-AX-001 | Auxiliary Steam | MOV-10LBC06-AA402: Motor operated isolation valve | MOV-10LBC06-AA402: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 289 MOV-10LBC06-AA402 S=4.
PB-SL-006-X-AX | PREVENTION | THR-AX-001 | Auxiliary Steam | TAH-10MAW82-CT055: Temperature alarm high (056 /057 /058 are available to alert | TAH-10MAW82-CT055: Temperature alarm high (056 /057 /058 are available to alert | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2186 TAH-10MAW82-CT055 S=5. Also protects STG Seals (PB-SL-006).
PB-SL-005-X-AX | PREVENTION | THR-AX-001 | Auxiliary Steam | TAL-10MAW82-CT055: Temperature alarm low (056 /057 /058 are available to alert | TAL-10MAW82-CT055: Temperature alarm low (056 /057 /058 are available to alert | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2178 TAL-10MAW82-CT055 S=5. Also protects STG Seals (PB-SL-005).
THR-AX-002 | THREAT | TE-AX-001 | Auxiliary Steam | Pressure excursion from PRV failure | Pressure excursion from PRV failure
MB-AX-001 | MITIGATION | TE-AX-001 | Auxiliary Steam | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-AX-003 | MITIGATION | TE-AX-001 | Auxiliary Steam | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-AX-004 | MITIGATION | TE-AX-001 | Auxiliary Steam | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-AX-002 | MITIGATION | TE-AX-001 | Auxiliary Steam | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-AX-001 | CONSEQUENCE | TE-AX-001 | Auxiliary Steam | Aux steam leak / scald | Aux steam leak / scald | [7 empty] | A | 3
MB-AX-005 | MITIGATION | CON-AX-001 | Auxiliary Steam | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-AX-002 | CONSEQUENCE | TE-AX-001 | Auxiliary Steam | Steam release causing equipment damage | Steam release causing equipment damage | [7 empty] | D | 4
HAZ-BY-001 | HAZARD |  | HRSG Bypass | HP/IP/LP bypass valves dumping steam to condenser during trip | Bypass pipework and desuperheater (Variable (up to 170 bar), Variable) Fluid: HP steam Location: HRSG Bypass
TE-BY-001 | TOP_EVENT | HAZ-BY-001 | HRSG Bypass | Loss of containment from HRSG bypass and casing | Loss of containment from HRSG bypass and casing
THR-BY-001 | THREAT | TE-BY-001 | HRSG Bypass | Bypass valve failure to open on turbine trip | Bypass valve failure to open on turbine trip
PB-BY-003 | PREVENTION | THR-BY-001 | HRSG Bypass | UPS power backup is available for 24 hours for control system. | UPS power backup is available for 24 hours for control system. | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1671 S=4.
PB-BY-002 | PREVENTION | THR-BY-001 | HRSG Bypass | PDAL XYMBR10-CP151/152 | PDAL XYMBR10-CP151/152 | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1628 S=4.
PB-BY-001 | PREVENTION | THR-BY-001 | HRSG Bypass | Operator-controlled flue gas supervision | Operator-controlled flue gas supervision | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1624 S=4.
THR-BY-002 | THREAT | TE-BY-001 | HRSG Bypass | Steam release from bypass valve body/bonnet leak | Steam release from bypass valve body/bonnet leak
MB-BY-001 | MITIGATION | TE-BY-001 | HRSG Bypass | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-BY-003 | MITIGATION | TE-BY-001 | HRSG Bypass | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-BY-004 | MITIGATION | TE-BY-001 | HRSG Bypass | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-BY-002 | MITIGATION | TE-BY-001 | HRSG Bypass | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-BY-001 | CONSEQUENCE | TE-BY-001 | HRSG Bypass | Steam jet injury to personnel | Steam jet injury to personnel | [7 empty] | A | 4
MB-BY-005 | MITIGATION | CON-BY-001 | HRSG Bypass | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-BY-002 | CONSEQUENCE | TE-BY-001 | HRSG Bypass | Pipe rupture and equipment damage | Pipe rupture and equipment damage | [7 empty] | D | 4
CON-BY-003 | CONSEQUENCE | TE-BY-001 | HRSG Bypass | Thermal burns / scald | Thermal burns / scald | [7 empty] | B | 4
HAZ-DB-001 | HAZARD |  | HRSG Duct Burner | Natural gas fired duct burner in HRSG | Duct burner fuel manifold, inside HRSG gas path (3-6 barg (fuel), HRSG exhaust temperature) Fluid: Natural gas Location: HRSG Duct Burner
TE-DB-001 | TOP_EVENT | HAZ-DB-001 | HRSG Duct Burner | Uncontrolled release from HRSG duct burner | Uncontrolled release from HRSG duct burner
THR-DB-001 | THREAT | TE-DB-001 | HRSG Duct Burner | Uncontrolled gas release from duct burner supply | 1. More flow of fuel gas from upstream
PB-DB-003 | PREVENTION | THR-DB-001 | HRSG Duct Burner | PRV-11HHG01-AA003: Pressure relief valve | PRV-11HHG01-AA003: Pressure relief valve | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1722 PRV-11HHG01-AA003 S=5.
PB-DB-005 | PREVENTION | THR-DB-001 | HRSG Duct Burner | NRV | NRV | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1733 S=5.
PB-DB-004 | PREVENTION | THR-DB-001 | HRSG Duct Burner | FCV-11HHG01-AA101: Flow control valve (control loop regulate downstream flow) | FCV-11HHG01-AA101: Flow control valve (control loop regulate downstream flow) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1725 FCV-11HHG01-AA101 S=5.
PB-DB-001 | PREVENTION | THR-DB-001 | HRSG Duct Burner | Instrument interlock: instrument interlock and START standby cooling air fan. | Instrument interlock: instrument interlock and START standby cooling air fan. | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1718 S=5.
THR-DB-002 | THREAT | TE-DB-001 | HRSG Duct Burner | Flame failure with delayed re-ignition attempt | Flame failure with delayed re-ignition attempt
PB-DB-002 | PREVENTION | THR-DB-002 | HRSG Duct Burner | Instrument interlock: instrument interlock and START standby cooling air fan. | Instrument interlock: instrument interlock and START standby cooling air fan. | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 1718 S=5.
MB-DB-001 | MITIGATION | TE-DB-001 | HRSG Duct Burner | Fire and gas detection system | Fire and gas detection system | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per NFPA 72 for detection system design; F&G philosophy per ISA TR84.00.07. Not in HAZOP; requires site validation. Ref: NFPA 72, ISA TR84.00.07.
MB-DB-002 | MITIGATION | TE-DB-001 | HRSG Duct Burner | F&G interlock to ESDV | F&G interlock to ESDV | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 for safety instrumented function; F&G logic per ISA TR84.00.07. Not in HAZOP; requires site validation. Ref: IEC 61511, ISA TR84.00.07.
MB-DB-007 | MITIGATION | TE-DB-001 | HRSG Duct Burner | Site emergency response plan | Site emergency response plan | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS RBPS Element 15 (Emergency Management); site ERP per local regulatory requirements. Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.15, local ERP regulation.
MB-DB-006 | MITIGATION | TE-DB-001 | HRSG Duct Burner | Hazardous area classification (IEC 60079) | Hazardous area classification (IEC 60079) | Hardware - Passive | MI Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-DB-001 | CONSEQUENCE | TE-DB-001 | HRSG Duct Burner | Jet fire | Jet fire | [7 empty] | E | 5
MB-DB-003 | MITIGATION | CON-DB-001 | HRSG Duct Burner | Firewater deluge / water spray system | Firewater deluge / water spray system | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per NFPA 15 for water spray fixed systems; coverage per NFPA 850 S6.4 for CCGT. Not in HAZOP; requires site validation. Ref: NFPA 15, NFPA 850 S6.4.
MB-DB-005 | MITIGATION | CON-DB-001 | HRSG Duct Burner | Fireproofing on structural steel (UL 1709) | Fireproofing on structural steel (UL 1709) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-DB-002 | CONSEQUENCE | TE-DB-001 | HRSG Duct Burner | Vapour cloud explosion | Vapour cloud explosion | [7 empty] | E | 5
MB-DB-004 | MITIGATION | CON-DB-002 | HRSG Duct Burner | Blast rated control room (API 752) | Blast rated control room (API 752) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-DB-003 | CONSEQUENCE | TE-DB-001 | HRSG Duct Burner | Flash fire | Flash fire | [7 empty] | A | 4
HAZ-FG-001 | HAZARD |  | Fuel Gas | Pressurised natural gas in fuel gas supply pipework | Pipework and skid volumes; typical 30-70 barg inventory (30-70 barg, Ambient) Fluid: Natural gas Location: Fuel Gas
TE-FG-001 | TOP_EVENT | HAZ-FG-001 | Fuel Gas | Loss of containment of natural gas from fuel gas system | Loss of containment of natural gas from fuel gas system
THR-FG-001 | THREAT | TE-FG-001 | Fuel Gas | Overpressure due to regulator failure or blocked outlet | 9. Blocked outlet on consumer side.
PB-FG-023 | PREVENTION | THR-FG-001 | Fuel Gas | Stack monitoring | Stack monitoring | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 2935 S=5.
PB-FG-042 | PREVENTION | THR-FG-001 | Fuel Gas | PAL-00QFB01-CP101A/B: Pressure alarm low (1oo2) | PAL-00QFB01-CP101A/B: Pressure alarm low (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3467 PAL-00QFB01-CP101A/B S=5.
PB-FG-040 | PREVENTION | THR-FG-001 | Fuel Gas | LSL-00EKC10-CL202: Level switch low (alert the operator) | LSL-00EKC10-CL202: Level switch low (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3430 LSL-00EKC10-CL202 S=5.
PB-FG-039 | PREVENTION | THR-FG-001 | Fuel Gas | BT00EKC10-BT001: alert the operator | BT00EKC10-BT001: alert the operator | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3411 BT00EKC10-BT001 S=5.
PB-FG-028 | PREVENTION | THR-FG-001 | Fuel Gas | PAL-00EKC50-CP101: Pressure alarm low (00EKC60-CP101 / 00EKC70-CP101 alert the | PAL-00EKC50-CP101: Pressure alarm low (00EKC60-CP101 / 00EKC70-CP101 alert the | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3071 PAL-00EKC50-CP101 S=5.
PB-FG-024 | PREVENTION | THR-FG-001 | Fuel Gas | LSH-11EKC30-CL202: Level switch high (A/B (1oo) | LSH-11EKC30-CL202: Level switch high (A/B (1oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3048 LSH-11EKC30-CL202 S=5.
THR-FG-002 | THREAT | TE-FG-001 | Fuel Gas | External corrosion / mechanical damage to pipework | 5. Electrical/Mechanical malfunctioning of block condensate tank transfer pump.
PB-FG-029 | PREVENTION | THR-FG-002 | Fuel Gas | Condensate transfer pump trip/run monitoring | Condensate transfer pump trip/run monitoring | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 3132 S=5.
THR-FG-003 | THREAT | TE-FG-001 | Fuel Gas | Flange or connection leak (vibration / thermal cycling) | 1. Fuel gas coil leakage in water bath heater.
PB-FG-037 | PREVENTION | THR-FG-003 | Fuel Gas | TAH-11EKC30-CT001: Temperature alarm high (A/B (1oo) | TAH-11EKC30-CT001: Temperature alarm high (A/B (1oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3338 TAH-11EKC30-CT001 S=5.
PB-FG-033 | PREVENTION | THR-FG-003 | Fuel Gas | TAL-11EKC30-CT001: Temperature alarm low (A/B (1oo) | TAL-11EKC30-CT001: Temperature alarm low (A/B (1oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3312 TAL-11EKC30-CT001 S=5.
PB-FG-032 | PREVENTION | THR-FG-003 | Fuel Gas | TAL-11EKC10-CT002: Temperature alarm low (A/B (1oo) | TAL-11EKC10-CT002: Temperature alarm low (A/B (1oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3304 TAL-11EKC10-CT002 S=5.
THR-FG-004 | THREAT | TE-FG-001 | Fuel Gas | Valve passing during maintenance or isolation | 13. Malfunctioning and closing of inlet guide valve vane PIC-00EKH41-AA133 (Section2).
PB-FG-041 | PREVENTION | THR-FG-004 | Fuel Gas | VALVE-00EKC10-AA402: Valve position confirmation ON/OFF | VALVE-00EKC10-AA402: Valve position confirmation ON/OFF | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3436 VALVE-00EKC10-AA402 S=5.
PB-FG-038 | PREVENTION | THR-FG-004 | Fuel Gas | VALVE-11EKT20-AA109: Valve position confirmation pneumatic ON/OFF | VALVE-11EKT20-AA109: Valve position confirmation pneumatic ON/OFF | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3348 VALVE-11EKT20-AA109 S=5.
PB-FG-036 | PREVENTION | THR-FG-004 | Fuel Gas | VALVE-11EKT20-AA113: Pneumatic control valve positioner | VALVE-11EKT20-AA113: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 3326 VALVE-11EKT20-AA113 S=5.
PB-FG-035 | PREVENTION | THR-FG-004 | Fuel Gas | VALVE-11EKT20-AA106: Valve position confirmation pneumatic ON/OFF | VALVE-11EKT20-AA106: Valve position confirmation pneumatic ON/OFF | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3318 VALVE-11EKT20-AA106 S=5.
PB-FG-034 | PREVENTION | THR-FG-004 | Fuel Gas | VALVE-11EKT20-AA101: Valve position confirmation pneumatic ON/OFF | VALVE-11EKT20-AA101: Valve position confirmation pneumatic ON/OFF | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3314 VALVE-11EKT20-AA101 S=5.
PB-FG-031 | PREVENTION | THR-FG-004 | Fuel Gas | VALVE-11EKT10-AA111: Pneumatic control valve positioner | VALVE-11EKT10-AA111: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 3287 VALVE-11EKT10-AA111 S=5.
MB-FG-001 | MITIGATION | TE-FG-001 | Fuel Gas | AAH-00EKC10-AI002: Gas detection alarm (20% LEL) | AAH-00EKC10-AI002: Gas detection alarm (20% LEL) | Hardware - Active | HSSE | EFFECTIVE |  |  | From HAZOP | Verified rows 2938 AAH-00EKC10-AI002 S=5.
MB-FG-002 | MITIGATION | TE-FG-001 | Fuel Gas | Fire and gas detection system | Fire and gas detection system | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per NFPA 72 for detection system design; F&G philosophy per ISA TR84.00.07. Not in HAZOP; requires site validation. Ref: NFPA 72, ISA TR84.00.07.
MB-FG-003 | MITIGATION | TE-FG-001 | Fuel Gas | F&G interlock to ESDV | F&G interlock to ESDV | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 for safety instrumented function; F&G logic per ISA TR84.00.07. Not in HAZOP; requires site validation. Ref: IEC 61511, ISA TR84.00.07.
MB-FG-004 | MITIGATION | TE-FG-001 | Fuel Gas | Firewater deluge / water spray system | Firewater deluge / water spray system | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per NFPA 15 for water spray fixed systems; coverage per NFPA 850 S6.4 for CCGT. Not in HAZOP; requires site validation. Ref: NFPA 15, NFPA 850 S6.4.
MB-FG-008 | MITIGATION | TE-FG-001 | Fuel Gas | Site emergency response plan | Site emergency response plan | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS RBPS Element 15 (Emergency Management); site ERP per local regulatory requirements. Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.15, local ERP regulation.
MB-FG-006 | MITIGATION | TE-FG-001 | Fuel Gas | Fireproofing on structural steel (UL 1709) | Fireproofing on structural steel (UL 1709) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-FG-001 | CONSEQUENCE | TE-FG-001 | Fuel Gas | Vapour cloud explosion in congested area | Vapour cloud explosion in congested area | [7 empty] | E | 5
MB-FG-005 | MITIGATION | CON-FG-001 | Fuel Gas | Blast rated control room (API 752) | Blast rated control room (API 752) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-FG-002 | CONSEQUENCE | TE-FG-001 | Fuel Gas | Equipment damage requiring forced outage | Equipment damage requiring forced outage | [7 empty] | D | 4
HAZ-FO-001 | HAZARD |  | Fuel Oil | Backup fuel oil (HFO / LFO) supply system | Tank + forwarding pipework (Up to 70 barg, Up to 140 deg C (HFO heated)) Fluid: Fuel oil Location: Fuel Oil
TE-FO-001 | TOP_EVENT | HAZ-FO-001 | Fuel Oil | Loss of containment of fuel oil | Loss of containment of fuel oil
THR-FO-001 | THREAT | TE-FO-001 | Fuel Oil | Flange leak from fuel oil pipework | 1. External fire in fuel oil storage tank dyke area.
THR-FO-002 | THREAT | TE-FO-001 | Fuel Oil | Tank overflow or overfill during delivery | Tank overflow or overfill during delivery
THR-FO-003 | THREAT | TE-FO-001 | Fuel Oil | Pump seal failure | Pump seal failure
MB-FO-001 | MITIGATION | TE-FO-001 | Fuel Oil | Gas detection system (from F&G) | Gas detection system (from F&G) | Hardware - Active | HSSE | EFFECTIVE |  |  | From HAZOP | Verified rows 998 MOVS-00EGC03-AA001 S=5.
MB-FO-006 | MITIGATION | TE-FO-001 | Fuel Oil | Spill response kit | Spill response kit | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site environmental management plan; spill kit specification per containment assessment. Not in HAZOP; requires site validation. Ref: ISO 14001, local environmental regulation.
MB-FO-007 | MITIGATION | TE-FO-001 | Fuel Oil | Site emergency response plan | Site emergency response plan | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS RBPS Element 15 (Emergency Management); site ERP per local regulatory requirements. Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.15, local ERP regulation.
MB-FO-004 | MITIGATION | TE-FO-001 | Fuel Oil | Bund containment around tank (API 650) | Bund containment around tank (API 650) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-FO-001 | CONSEQUENCE | TE-FO-001 | Fuel Oil | Jet fire | Jet fire | [7 empty] | E | 5
MB-FO-002 | MITIGATION | CON-FO-001 | Fuel Oil | Flame / fire detection (from F&G) | Flame / fire detection (from F&G) | Hardware - Active | HSSE | EFFECTIVE |  |  | From HAZOP | Verified rows 998 MOVS-00EGC03-AA001 S=5.
MB-FO-003 | MITIGATION | CON-FO-001 | Fuel Oil | Fire detection in oil area | Fire detection in oil area | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per NFPA 72 for fire detection system design. Not in HAZOP; requires site validation. Ref: NFPA 72.
MB-FO-005 | MITIGATION | CON-FO-001 | Fuel Oil | Fire suppression (CO2 / water spray) | Fire suppression (CO2 / water spray) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-FO-002 | CONSEQUENCE | TE-FO-001 | Fuel Oil | Vapour cloud explosion | Vapour cloud explosion | [7 empty] | E | 5
CON-FO-003 | CONSEQUENCE | TE-FO-001 | Fuel Oil | Flash fire | Flash fire | [7 empty] | A | 4
HAZ-FW-001 | HAZARD |  | Feedwater | High pressure boiler feedwater | Feedwater pipework and deaerator (170+ bar, Up to 170 deg C) Fluid: HP feedwater Location: Feedwater
TE-FW-001 | TOP_EVENT | HAZ-FW-001 | Feedwater | Loss of containment from feedwater system | Loss of containment from feedwater system
THR-FW-001 | THREAT | TE-FW-001 | Feedwater | BFP discharge pipe rupture (high energy) | 7. Malfunctioning and closure of MOV 11LAB02-AA002 / 11LAB03-AA002 on HP discharge header (TYPICAL).
PB-FW-008 | PREVENTION | THR-FW-001 | Feedwater | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 541 S=5.
PB-FW-007 | PREVENTION | THR-FW-001 | Feedwater | TCV-11LAE05-AA101: Temperature control valve (Confirmed OPEN/CLOSE/Discrepancy | TCV-11LAE05-AA101: Temperature control valve (Confirmed OPEN/CLOSE/Discrepancy | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 532 TCV-11LAE05-AA101 S=5.
PB-FW-006 | PREVENTION | THR-FW-001 | Feedwater | VALVE-11LAE05-AA004: Valve position feedback | VALVE-11LAE05-AA004: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 508 VALVE-11LAE05-AA004 S=5.
PB-FW-005 | PREVENTION | THR-FW-001 | Feedwater | MOV-11LAB02-AA004: Motor operated isolation valve | MOV-11LAB02-AA004: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 500 MOV-11LAB02-AA004 S=5.
PB-FW-004 | PREVENTION | THR-FW-001 | Feedwater | MOV-11LAB02-AA002: Motor operated isolation valve | MOV-11LAB02-AA002: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 489 MOV-11LAB02-AA002 S=5.
PB-FW-003 | PREVENTION | THR-FW-001 | Feedwater | VALVE-11LAB02-AA101: Valve position feedback | VALVE-11LAB02-AA101: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 484 VALVE-11LAB02-AA101 S=5.
THR-FW-002 | THREAT | TE-FW-001 | Feedwater | Feedwater chemistry excursion causing tube damage | Feedwater chemistry excursion causing tube damage
PB-FW-009 | PREVENTION | THR-FW-002 | Feedwater | Online SWAS feedwater quality analysis | Online SWAS feedwater quality analysis | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 543 S=5.
PB-FW-002 | PREVENTION | THR-FW-002 | Feedwater | PDAH-11LAB02-CP181: Differential pressure alarm high (11LAB03-CP181 alert the | PDAH-11LAB02-CP181: Differential pressure alarm high (11LAB03-CP181 alert the | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 454 PDAH-11LAB02-CP181 S=5.
PB-FW-001 | PREVENTION | THR-FW-002 | Feedwater | FAL-11LAB01-CF101A/B: Flow alarm low (1oo2) | FAL-11LAB01-CF101A/B: Flow alarm low (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 433 FAL-11LAB01-CF101A/B S=5.
MB-FW-003 | MITIGATION | TE-FW-001 | Feedwater | Emergency isolation valve | Emergency isolation valve | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-FW-004 | MITIGATION | TE-FW-001 | Feedwater | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-FW-001 | MITIGATION | TE-FW-001 | Feedwater | Leak detection and area drainage | Leak detection and area drainage | Hardware - Passive | MI Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site process safety management system; detection method per fluid and environment. Not in HAZOP; requires site validation. Ref: IEC 61511, site SMS.
MB-FW-002 | MITIGATION | TE-FW-001 | Feedwater | Access restriction to BFP area | Access restriction to BFP area | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-FW-001 | CONSEQUENCE | TE-FW-001 | Feedwater | Pipe rupture and equipment damage | Pipe rupture and equipment damage | [7 empty] | D | 3
CON-FW-002 | CONSEQUENCE | TE-FW-001 | Feedwater | Major equipment failure with escalation potential | Major equipment failure with escalation potential | [7 empty] | E | 5
HAZ-GH-001 | HAZARD |  | Generator H2 | Hydrogen cooling gas in generator casing | Generator internal volume at 3-5 barg H2 (3-5 barg, Ambient to 60 deg C) Fluid: Hydrogen Location: Generator H2
TE-GH-001 | TOP_EVENT | HAZ-GH-001 | Generator H2 | Uncontrolled release of hydrogen from generator | Uncontrolled release of hydrogen from generator
THR-GH-001 | THREAT | TE-GH-001 | Generator H2 | Seal failure allowing H2 escape to atmosphere | Seal failure allowing H2 escape to atmosphere
PB-GH-003 | PREVENTION | THR-GH-001 | Generator H2 | PSL10MKG21-CP101: alert the operator | PSL10MKG21-CP101: alert the operator | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2387 PSL10MKG21-CP101 S=5. Also protects STG Seals (PB-SL-012).
PB-GH-002 | PREVENTION | THR-GH-001 | Generator H2 | PSH10MKG21-CP102: alert the operator | PSH10MKG21-CP102: alert the operator | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2373 PSH10MKG21-CP102 S=5.
PB-GH-001 | PREVENTION | THR-GH-001 | Generator H2 | PAL-00PGB07-CP101A/B: Pressure alarm low (1oo2) | PAL-00PGB07-CP101A/B: Pressure alarm low (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2362 PAL-00PGB07-CP101A/B S=5.
THR-GH-002 | THREAT | TE-GH-001 | Generator H2 | H2 purity loss (air ingress into casing) | H2 purity loss (air ingress into casing)
THR-GH-003 | THREAT | TE-GH-001 | Generator H2 | Overpressure from H2 supply regulator failure | 1. No /Less supply of CCCW from upstream
PB-GH-005 | PREVENTION | THR-GH-003 | Generator H2 | PSV-10MKG42-AA191: release excess pressure above [TBC] BARG to safe location | PSV-10MKG42-AA191: release excess pressure above [TBC] BARG to safe location | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2448 PSV-10MKG42-AA191 S=5.
PB-GH-004 | PREVENTION | THR-GH-003 | Generator H2 | PSV-10MKG10-AA191: 10MKG01-AA191 release excess pressure above 210 BARG to | PSV-10MKG10-AA191: 10MKG01-AA191 release excess pressure above 210 BARG to | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2446 PSV-10MKG10-AA191 S=5.
MB-GH-001 | MITIGATION | TE-GH-001 | Generator H2 | H2-specific catalytic detector | H2-specific catalytic detector | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 60079-29-1 for hydrogen detection; catalytic/electrochemical sensor selection per EN 50073. Not in HAZOP; requires site validation. Ref: IEC 60079-29-1, EN 50073.
MB-GH-002 | MITIGATION | TE-GH-001 | Generator H2 | Ventilation system with gas interlock | Ventilation system with gas interlock | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 60079-10-1 for ventilation in hazardous areas; air change rate per ATEX assessment. Not in HAZOP; requires site validation. Ref: IEC 60079-10-1, ATEX directive.
MB-GH-005 | MITIGATION | TE-GH-001 | Generator H2 | Hazardous area classification (IEC 60079) | Hazardous area classification (IEC 60079) | Hardware - Passive | MI Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-GH-001 | CONSEQUENCE | TE-GH-001 | Generator H2 | Hydrogen explosion in generator building | Hydrogen explosion in generator building | [7 empty] | E | 5
MB-GH-003 | MITIGATION | CON-GH-001 | Generator H2 | Explosion relief panels | Explosion relief panels | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-GH-004 | MITIGATION | CON-GH-001 | Generator H2 | Blast-rated generator building (API 752) | Blast-rated generator building (API 752) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
HAZ-HI-001 | HAZARD |  | HRSG IP | IP water/steam in HRSG IP section | IP drum + IP economiser + IP evaporator + IP superheater (30-50 bar, 230-360 deg C) Fluid: IP water and steam Location: HRSG IP
TE-HI-001 | TOP_EVENT | HAZ-HI-001 | HRSG IP | Loss of containment from HRSG IP section | Loss of containment from HRSG IP section
THR-HI-001 | THREAT | TE-HI-001 | HRSG IP | IP section tube leak from FAC or corrosion | 8. Malfunctioning and closure of MOV 11LBC10-AA101 on HP steam turbine outlet to IP system.
PB-HI-012 | PREVENTION | THR-HI-001 | HRSG IP | NRV-11LBA20-AA201: Non-return valve | NRV-11LBA20-AA201: Non-return valve | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1390 NRV-11LBA20-AA201 S=5. Also protects HP Steam (NRV-11LBA20-AA201).
PB-HI-015 | PREVENTION | THR-HI-001 | HRSG IP | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1408 S=5.
PB-HI-013 | PREVENTION | THR-HI-001 | HRSG IP | Annual preventive maintenance schedule | Annual preventive maintenance schedule | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1396 S=5.
PB-HI-014 | PREVENTION | THR-HI-001 | HRSG IP | VALVE-11HAC30-AA101: Pneumatic control valve positioner | VALVE-11HAC30-AA101: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 1399 VALVE-11HAC30-AA101 S=5.
PB-HI-011 | PREVENTION | THR-HI-001 | HRSG IP | LAH-11HAD20-CL121: Level alarm high (A/B/C (2oo) | LAH-11HAD20-CL121: Level alarm high (A/B/C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1381 LAH-11HAD20-CL121 S=5. Also protects HRSG HP (LAH-11HAD20-CL121).
PB-HI-010 | PREVENTION | THR-HI-001 | HRSG IP | MOV-11LBB10-AA102: Motor operated isolation valve | MOV-11LBB10-AA102: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1371 MOV-11LBB10-AA102 S=5.
THR-HI-002 | THREAT | TE-HI-001 | HRSG IP | Thermal stress during startup/shutdown transitions | Thermal stress during startup/shutdown transitions
MB-HI-001 | MITIGATION | TE-HI-001 | HRSG IP | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-HI-003 | MITIGATION | TE-HI-001 | HRSG IP | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-HI-004 | MITIGATION | TE-HI-001 | HRSG IP | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-HI-002 | MITIGATION | TE-HI-001 | HRSG IP | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-HI-001 | CONSEQUENCE | TE-HI-001 | HRSG IP | Tube rupture and IP steam release | Tube rupture and IP steam release | [7 empty] | D | 4
MB-HI-005 | MITIGATION | CON-HI-001 | HRSG IP | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-HI-002 | CONSEQUENCE | TE-HI-001 | HRSG IP | Major equipment failure with escalation potential | Major equipment failure with escalation potential | [7 empty] | E | 5
HAZ-HL-001 | HAZARD |  | HRSG LP | LP water/steam in HRSG LP section | LP drum + LP evaporator + LP economiser (4-10 bar, 150-220 deg C) Fluid: LP water and steam Location: HRSG LP
TE-HL-001 | TOP_EVENT | HAZ-HL-001 | HRSG LP | Loss of containment from HRSG LP section | Loss of containment from HRSG LP section
THR-HL-001 | THREAT | TE-HL-001 | HRSG LP | LP tube leak from FAC or corrosion | 16. Malfunctioning and closure of MOV 11LBA30-AA104 (LP steam HRSG isolation valve).
PB-HL-013 | PREVENTION | THR-HL-001 | HRSG LP | NRV-11LBA10-AA201: Non-return valve | NRV-11LBA10-AA201: Non-return valve | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1548 NRV-11LBA10-AA201 S=5. Also protects HP Steam (NRV-11LBA10-AA201).
PB-HL-017 | PREVENTION | THR-HL-001 | HRSG LP | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1573 S=5.
PB-HL-015 | PREVENTION | THR-HL-001 | HRSG LP | Annual preventive maintenance schedule | Annual preventive maintenance schedule | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1558 S=5.
PB-HL-016 | PREVENTION | THR-HL-001 | HRSG LP | VALVE-11LAB61-AA102: Pneumatic control valve positioner | VALVE-11LAB61-AA102: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 1564 VALVE-11LAB61-AA102 S=5. Also protects Feedwater (VALVE-11LAB61-AA102).
PB-HL-014 | PREVENTION | THR-HL-001 | HRSG LP | VALVE-11LAB63-AA101: Pneumatic control valve positioner | VALVE-11LAB63-AA101: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 1554 VALVE-11LAB63-AA101 S=5. Also protects Feedwater (VALVE-11LAB63-AA101).
PB-HL-011 | PREVENTION | THR-HL-001 | HRSG LP | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo) | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1543 PAH-11HAD30-CP121 S=5. Also protects HRSG HP (PAH-11HAD30-CP121).
THR-HL-002 | THREAT | TE-HL-001 | HRSG LP | Overpressure from stuck LP drum safety valve | 5. Malfunctioning and closure of pneumatic control valve 11LCA20-AA103 on demand.
PB-HL-009 | PREVENTION | THR-HL-002 | HRSG LP | PSV-11LBA30-AA191: PSV set (PSV-11HAD30-AA191 and 11HAD30-AA192 | PSV-11LBA30-AA191: PSV set (PSV-11HAD30-AA191 and 11HAD30-AA192 | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1526 PSV-11LBA30-AA191 S=5. Also protects HP Steam (PSV-11LBA30-AA191).
PB-HL-012 | PREVENTION | THR-HL-002 | HRSG LP | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo) | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1543 PAH-11HAD30-CP121 S=5. Also protects HRSG HP (PAH-11HAD30-CP121).
MB-HL-001 | MITIGATION | TE-HL-001 | HRSG LP | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-HL-003 | MITIGATION | TE-HL-001 | HRSG LP | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-HL-004 | MITIGATION | TE-HL-001 | HRSG LP | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-HL-002 | MITIGATION | TE-HL-001 | HRSG LP | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-HL-001 | CONSEQUENCE | TE-HL-001 | HRSG LP | LP steam release (scald hazard) | LP steam release (scald hazard) | [7 empty] | A | 3
MB-HL-005 | MITIGATION | CON-HL-001 | HRSG LP | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-HL-002 | CONSEQUENCE | TE-HL-001 | HRSG LP | Major equipment failure with escalation potential | Major equipment failure with escalation potential | [7 empty] | E | 5
HAZ-HP-001 | HAZARD |  | HP Steam | High pressure superheated steam in HP steam header | Approx 12 t stored in pipework and HRSG HP drums (100-170 bar, 540-565 deg C) Fluid: HP steam Location: HP Steam
TE-HP-001 | TOP_EVENT | HAZ-HP-001 | HP Steam | Loss of containment of HP steam | Loss of containment of HP steam
THR-HP-001 | THREAT | TE-HP-001 | HP Steam | Overpressure due to blocked outlet or regulator failure | 3. Blocked outlet on HP steam inlet 1/2 to turbine on demand.
PB-HP-010 | PREVENTION | THR-HP-001 | HP Steam | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 72 S=4.
PB-HP-009 | PREVENTION | THR-HP-001 | HP Steam | High alarm with instrument interlock (auto-trip) | High alarm with instrument interlock (auto-trip) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 69 S=4.
PB-HP-006 | PREVENTION | THR-HP-001 | HP Steam | FOR10LBA01-AA409: Valve position feedback | FOR10LBA01-AA409: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 56 FOR10LBA01-AA409 S=4.
PB-HP-005 | PREVENTION | THR-HP-001 | HP Steam | VALVE-11LBA02-AA101: Valve position feedback | VALVE-11LBA02-AA101: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 43 VALVE-11LBA02-AA101 S=4.
PB-HP-004 | PREVENTION | THR-HP-001 | HP Steam | FOR11LBA02-AA001: Valve position feedback | FOR11LBA02-AA001: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 35 FOR11LBA02-AA001 S=4.
PB-HP-003 | PREVENTION | THR-HP-001 | HP Steam | PAH-10LBA03-CP121A/B: Pressure alarm high (1oo2) | PAH-10LBA03-CP121A/B: Pressure alarm high (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 23 PAH-10LBA03-CP121A/B S=4.
THR-HP-002 | THREAT | TE-HP-001 | HP Steam | Condensate accumulation and water hammer | 1. Incorrect dosing of chemicals to BFW/steam drum/DM water quality, etc.
PB-HP-007 | PREVENTION | THR-HP-002 | HP Steam | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow. | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow. | Hardware - Passive | MI Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 61 S=4.
THR-HP-003 | THREAT | TE-HP-001 | HP Steam | Reverse flow during HRSG maintenance | 1. No / less flow from upstream HRSG for Unit 11 / Unit 12 / Unit 13.
PB-HP-008 | PREVENTION | THR-HP-003 | HP Steam | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow. | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow. | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 61 S=4.
PB-HP-002 | PREVENTION | THR-HP-003 | HP Steam | MOV: Motor operated isolation valve | MOV: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 7 S=4.
THR-HP-004 | THREAT | TE-HP-001 | HP Steam | Thermal overstress during startup/shutdown | Thermal overstress during startup/shutdown
MB-HP-001 | MITIGATION | TE-HP-001 | HP Steam | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-HP-003 | MITIGATION | TE-HP-001 | HP Steam | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-HP-004 | MITIGATION | TE-HP-001 | HP Steam | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-HP-002 | MITIGATION | TE-HP-001 | HP Steam | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-HP-001 | CONSEQUENCE | TE-HP-001 | HP Steam | Steam jet injury to personnel | Steam jet injury to personnel | [7 empty] | A | 4
MB-HP-005 | MITIGATION | CON-HP-001 | HP Steam | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-HP-002 | CONSEQUENCE | TE-HP-001 | HP Steam | Pipe rupture and equipment damage | Pipe rupture and equipment damage | [7 empty] | D | 4
CON-HP-003 | CONSEQUENCE | TE-HP-001 | HP Steam | Steam release causing equipment damage | Steam release causing equipment damage | [7 empty] | D | 4
HAZ-HR-001 | HAZARD |  | HRSG HP | HP water/steam in HRSG HP section (economiser, evaporator, superheater) | HP drum + HP economiser + HP evaporator + HP superheater (100-170 bar, 310-565 deg C) Fluid: HP water and steam Location: HRSG HP
TE-HR-001 | TOP_EVENT | HAZ-HR-001 | HRSG HP | Loss of containment from HRSG HP section | Loss of containment from HRSG HP section
THR-HR-001 | THREAT | TE-HR-001 | HRSG HP | Tube failure (creep / FAC / corrosion) | Tube failure (creep / FAC / corrosion)
PB-HR-015 | PREVENTION | THR-HR-001 | HRSG HP | NRV-11LBA10-AA201: Non-return valve | NRV-11LBA10-AA201: Non-return valve | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1235 NRV-11LBA10-AA201 S=4. Also protects HP Steam (NRV-11LBA10-AA201).
PB-HR-018 | PREVENTION | THR-HR-001 | HRSG HP | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1262 S=4.
PB-HR-017 | PREVENTION | THR-HR-001 | HRSG HP | Annual preventive maintenance schedule | Annual preventive maintenance schedule | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1247 S=4.
PB-HR-014 | PREVENTION | THR-HR-001 | HRSG HP | LAH-11HAD10-CL121: Level alarm high (A/B/C (2oo) | LAH-11HAD10-CL121: Level alarm high (A/B/C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1226 LAH-11HAD10-CL121 S=4.
PB-HR-012 | PREVENTION | THR-HR-001 | HRSG HP | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo) | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1223 PAH-11HAD10-CP121A/B S=4.
PB-HR-011 | PREVENTION | THR-HR-001 | HRSG HP | MOV-11LBA10-AA102: Motor operated isolation valve | MOV-11LBA10-AA102: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1210 MOV-11LBA10-AA102 S=4. Also protects HP Steam (MOV-11LBA10-AA102).
THR-HR-002 | THREAT | TE-HR-001 | HRSG HP | Feedwater chemistry excursion (caustic/acid attack) | Feedwater chemistry excursion (caustic/acid attack)
THR-HR-003 | THREAT | TE-HR-001 | HRSG HP | Thermal stress during startup/shutdown transitions | Thermal stress during startup/shutdown transitions
THR-HR-004 | THREAT | TE-HR-001 | HRSG HP | Overpressure from blocked safety valve or stuck bypass | 2. Malfunctioning and closure of pneumatic control valve 11LAB61-AA102 / 11LAB61-AA101.
PB-HR-016 | PREVENTION | THR-HR-004 | HRSG HP | VALVE-11LAB63-AA101: Pneumatic control valve positioner | VALVE-11LAB63-AA101: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 1239 VALVE-11LAB63-AA101 S=4. Also protects Feedwater (VALVE-11LAB63-AA101).
PB-HR-013 | PREVENTION | THR-HR-004 | HRSG HP | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo) | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1223 PAH-11HAD10-CP121A/B S=4.
PB-HR-009 | PREVENTION | THR-HR-004 | HRSG HP | VALVE-11LAE10-AA102: Pneumatic control valve positioner | VALVE-11LAE10-AA102: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 1199 VALVE-11LAE10-AA102 S=4. Also protects Feedwater (VALVE-11LAE10-AA102).
PB-HR-008 | PREVENTION | THR-HR-004 | HRSG HP | PDAH-11LAE40-CF181: Differential pressure alarm high (alert the operator) | PDAH-11LAE40-CF181: Differential pressure alarm high (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1189 PDAH-11LAE40-CF181 S=4. Also protects Feedwater (PDAH-11LAE40-CF181).
PB-HR-007 | PREVENTION | THR-HR-004 | HRSG HP | VALVE-11LAE10-AA104: Pneumatic control valve positioner | VALVE-11LAE10-AA104: Pneumatic control valve positioner | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | From HAZOP | Verified rows 1181 VALVE-11LAE10-AA104 S=4. Also protects Feedwater (VALVE-11LAE10-AA104).
PB-HR-005 | PREVENTION | THR-HR-004 | HRSG HP | PDAH-11LAE10-CP181: Differential pressure alarm high (alert the operator) | PDAH-11LAE10-CP181: Differential pressure alarm high (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1169 PDAH-11LAE10-CP181 S=4. Also protects Feedwater (PDAH-11LAE10-CP181).
MB-HR-001 | MITIGATION | TE-HR-001 | HRSG HP | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-HR-003 | MITIGATION | TE-HR-001 | HRSG HP | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-HR-004 | MITIGATION | TE-HR-001 | HRSG HP | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-HR-002 | MITIGATION | TE-HR-001 | HRSG HP | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-HR-001 | CONSEQUENCE | TE-HR-001 | HRSG HP | HRSG casing damage / tube failure | HRSG casing damage / tube failure | [7 empty] | D | 4
CON-HR-002 | CONSEQUENCE | TE-HR-001 | HRSG HP | HP steam release internal to HRSG casing | HP steam release internal to HRSG casing | [7 empty] | D | 4
MB-HR-005 | MITIGATION | CON-HR-002 | HRSG HP | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
HAZ-LP-001 | HAZARD |  | LP Steam | LP steam header distribution | LP steam pipework (4-10 bar, 150-220 deg C) Fluid: LP steam Location: LP Steam
TE-LP-001 | TOP_EVENT | HAZ-LP-001 | LP Steam | Loss of containment of LP steam | Loss of containment of LP steam
THR-LP-001 | THREAT | TE-LP-001 | LP Steam | LP steam line leak at flanged connection | 3. Blocked outlet on LP steam inlet to turbine on demand.
PB-LP-006 | PREVENTION | THR-LP-001 | LP Steam | NRV is provided in discharge LP steam line of each HRSG to prevent reverse flow. | NRV is provided in discharge LP steam line of each HRSG to prevent reverse flow. | Hardware - Passive | MI Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 231 S=4.
PB-LP-008 | PREVENTION | THR-LP-001 | LP Steam | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 246 S=4.
PB-LP-007 | PREVENTION | THR-LP-001 | LP Steam | LABLE11LBA30-CT121: Temperature elements are avai A/B (1oo2)to generate high | LABLE11LBA30-CT121: Temperature elements are avai A/B (1oo2)to generate high | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 243 LABLE11LBA30-CT121 S=4. Also protects HP Steam (LABLE11LBA30-CT121).
PB-LP-005 | PREVENTION | THR-LP-001 | LP Steam | FOR10LBD02-AA405: Valve position feedback | FOR10LBD02-AA405: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 227 FOR10LBD02-AA405 S=4.
PB-LP-004 | PREVENTION | THR-LP-001 | LP Steam | MOV-11LBD01-AA402: Motor operated isolation valve | MOV-11LBD01-AA402: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 223 MOV-11LBD01-AA402 S=4.
PB-LP-001 | PREVENTION | THR-LP-001 | LP Steam | MOV-11LBD01-AA001: Motor operated isolation valve | MOV-11LBD01-AA001: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 190 MOV-11LBD01-AA001 S=4.
THR-LP-002 | THREAT | TE-LP-001 | LP Steam | LP PRV failure to reseat after overpressure event | LP PRV failure to reseat after overpressure event
PB-LP-003 | PREVENTION | THR-LP-002 | LP Steam | PCV-11LBD02-AA101: Pressure control valve (Confirmed OPEN/CLOSE/Discrepancy | PCV-11LBD02-AA101: Pressure control valve (Confirmed OPEN/CLOSE/Discrepancy | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 215 PCV-11LBD02-AA101 S=4.
PB-LP-002 | PREVENTION | THR-LP-002 | LP Steam | PAH-10LBD02-CP101A/B: Pressure alarm high (1oo2) | PAH-10LBD02-CP101A/B: Pressure alarm high (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 206 PAH-10LBD02-CP101A/B S=4.
MB-LP-001 | MITIGATION | TE-LP-001 | LP Steam | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-LP-003 | MITIGATION | TE-LP-001 | LP Steam | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-LP-004 | MITIGATION | TE-LP-001 | LP Steam | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-LP-002 | MITIGATION | TE-LP-001 | LP Steam | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-LP-001 | CONSEQUENCE | TE-LP-001 | LP Steam | LP steam leak / scald | LP steam leak / scald | [7 empty] | A | 3
MB-LP-005 | MITIGATION | CON-LP-001 | LP Steam | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-LP-002 | CONSEQUENCE | TE-LP-001 | LP Steam | Steam release causing equipment damage | Steam release causing equipment damage | [7 empty] | D | 4
HAZ-NH-001 | HAZARD |  | Ammonia/SCR | Aqueous ammonia (19-25%) for SCR injection | Storage tank plus distribution pipework (Ambient to 3 barg, Ambient) Fluid: Aqueous ammonia Location: Ammonia/SCR
TE-NH-001 | TOP_EVENT | HAZ-NH-001 | Ammonia/SCR | Uncontrolled release of ammonia | Uncontrolled release of ammonia
THR-NH-001 | THREAT | TE-NH-001 | Ammonia/SCR | Transfer hose failure during unloading | 1. Leak rupture of unloading hose during ammonia unloading.
PB-NH-001 | PREVENTION | THR-NH-001 | Ammonia/SCR | Operator continuous attendance (manual control) | Operator continuous attendance (manual control) | Human - Active | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1745 S=4.
PB-NH-004 | PREVENTION | THR-NH-001 | Ammonia/SCR | VALVE-10GHD41-AA102: Valve position feedback | VALVE-10GHD41-AA102: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1841 VALVE-10GHD41-AA102 S=4.
PB-NH-003 | PREVENTION | THR-NH-001 | Ammonia/SCR | VALVE-10GHD41-AA104: Valve position feedback | VALVE-10GHD41-AA104: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1833 VALVE-10GHD41-AA104 S=4.
PB-NH-002 | PREVENTION | THR-NH-001 | Ammonia/SCR | VALVE-10GHD41-AA103: Valve position feedback | VALVE-10GHD41-AA103: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 1830 VALVE-10GHD41-AA103 S=4.
THR-NH-002 | THREAT | TE-NH-001 | Ammonia/SCR | Pipework leak in ammonia distribution system | Pipework leak in ammonia distribution system
THR-NH-003 | THREAT | TE-NH-001 | Ammonia/SCR | Tank overfill or overpressure | Tank overfill or overpressure
MB-NH-001 | MITIGATION | TE-NH-001 | Ammonia/SCR | Toxic gas detection (NH3) | Toxic gas detection (NH3) | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 60079-29-1 for flammable gas detection; placement per ISA TR84.00.07. Not in HAZOP; requires site validation. Ref: IEC 60079-29-1, ISA TR84.00.07.
MB-NH-003 | MITIGATION | TE-NH-001 | Ammonia/SCR | SCBA availability at unloading bay | SCBA availability at unloading bay | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per OSHA 29 CFR 1910.134 respiratory protection; SCBA stations per emergency escape analysis. Not in HAZOP; requires site validation. Ref: OSHA 1910.134, local OHS regulation.
MB-NH-004 | MITIGATION | TE-NH-001 | Ammonia/SCR | Emergency shower and eyewash | Emergency shower and eyewash | Hardware - Active | HSSE | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-NH-006 | MITIGATION | TE-NH-001 | Ammonia/SCR | Site emergency response plan | Site emergency response plan | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS RBPS Element 15 (Emergency Management); site ERP per local regulatory requirements. Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.15, local ERP regulation.
MB-NH-005 | MITIGATION | TE-NH-001 | Ammonia/SCR | Exclusion zone during transfers | Exclusion zone during transfers | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone radius per consequence modelling or prescriptive rule. Not in HAZOP; requires site validation. Ref: Site SMS, local OHS regulation.
CON-NH-001 | CONSEQUENCE | TE-NH-001 | Ammonia/SCR | Toxic ammonia vapour cloud | Toxic ammonia vapour cloud | [7 empty] | A | 4
MB-NH-002 | MITIGATION | CON-NH-001 | Ammonia/SCR | Water curtain / spray system | Water curtain / spray system | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Vapor Cloud Mitigation; water curtain design for NH3 knockdown. Not in HAZOP; requires site validation. Ref: CCPS vapor cloud mitigation guidelines.
HAZ-SS-001 | HAZARD |  | STG Steam | HP/IP/LP steam within steam turbine casing | Turbine internals and gland steam (Up to 170 bar, Up to 565 deg C) Fluid: HP steam Location: STG Steam
TE-SS-001 | TOP_EVENT | HAZ-SS-001 | STG Steam | Loss of containment from steam turbine | Loss of containment from steam turbine
THR-SS-001 | THREAT | TE-SS-001 | STG Steam | HP/IP/LP steam leak at turbine casing joint | 1. No / Less flow of auxiliary steam during warm up operation from upstream.
PB-SS-004 | PREVENTION | THR-SS-001 | STG Steam | Operator continuous attendance (manual control) | Operator continuous attendance (manual control) | Human - Active | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 1917 S=4.
PB-SS-023 | PREVENTION | THR-SS-001 | STG Steam | PCV: Pressure control valve (LCE81-AA001 is available in upstream to regulate | PCV: Pressure control valve (LCE81-AA001 is available in upstream to regulate | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2110 S=4.
PB-SS-022 | PREVENTION | THR-SS-001 | STG Steam | PCV-10LCE81-AA001: Pressure control valve (Field positioner / Discrepancy | PCV-10LCE81-AA001: Pressure control valve (Field positioner / Discrepancy | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2100 PCV-10LCE81-AA001 S=4. Also protects LP Steam (PCV-10LCE81-AA001).
PB-SS-021 | PREVENTION | THR-SS-001 | STG Steam | PDAH-10LCE81-CP122: Differential pressure alarm high (alert the operator) | PDAH-10LCE81-CP122: Differential pressure alarm high (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2094 PDAH-10LCE81-CP122 S=4. Also protects LP Steam (PDAH-10LCE81-CP122).
PB-SS-020 | PREVENTION | THR-SS-001 | STG Steam | TAH-10MAC81-CT053A/B: Temperature alarm high (C (2oo) | TAH-10MAC81-CT053A/B: Temperature alarm high (C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2089 TAH-10MAC81-CT053A/B S=4. Also protects ACC (TAH-10MAC81-CT053A/B).
PB-SS-019 | PREVENTION | THR-SS-001 | STG Steam | FCV: Flow control valve (Field positioner / Discrepancy position feedback | FCV: Flow control valve (Field positioner / Discrepancy position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2073 S=4.
THR-SS-002 | THREAT | TE-SS-001 | STG Steam | Gland steam system failure causing external leak | 6. Blocked outlet at Cold Reheat System during normal operation.
PB-SS-028 | PREVENTION | THR-SS-002 | STG Steam | MV10MAL95-AA401: Valve position feedback | MV10MAL95-AA401: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2220 MV10MAL95-AA401 S=4.
PB-SS-027 | PREVENTION | THR-SS-002 | STG Steam | MV10MAL87-AA401: Valve position feedback | MV10MAL87-AA401: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2215 MV10MAL87-AA401 S=4.
PB-SS-026 | PREVENTION | THR-SS-002 | STG Steam | MV10MAL82-AA401: Valve position feedback | MV10MAL82-AA401: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2210 MV10MAL82-AA401 S=4.
PB-SS-025 | PREVENTION | THR-SS-002 | STG Steam | MV10MAL83-AA401: Valve position feedback | MV10MAL83-AA401: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2205 MV10MAL83-AA401 S=4.
PB-SS-024 | PREVENTION | THR-SS-002 | STG Steam | MV10MAL81-AA401: Valve position feedback | MV10MAL81-AA401: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2200 MV10MAL81-AA401 S=4.
PB-SS-018 | PREVENTION | THR-SS-002 | STG Steam | MV10MAL86-AA401: Valve position feedback | MV10MAL86-AA401: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2049 MV10MAL86-AA401 S=4.
THR-SS-003 | THREAT | TE-SS-001 | STG Steam | Valve stem leak on extraction or admission valves | 2. Malfunctioning and closure of solenoid valve 10SCB81-AA005 on demand.
MB-SS-001 | MITIGATION | TE-SS-001 | STG Steam | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-SS-003 | MITIGATION | TE-SS-001 | STG Steam | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-SS-004 | MITIGATION | TE-SS-001 | STG Steam | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-SS-002 | MITIGATION | TE-SS-001 | STG Steam | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-SS-001 | CONSEQUENCE | TE-SS-001 | STG Steam | Steam jet injury | Steam jet injury | [7 empty] | A | 4
MB-SS-005 | MITIGATION | CON-SS-001 | STG Steam | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-SS-002 | CONSEQUENCE | TE-SS-001 | STG Steam | Turbine damage | Turbine damage | [7 empty] | D | 4
CON-SS-003 | CONSEQUENCE | TE-SS-001 | STG Steam | Steam release causing equipment damage | Steam release causing equipment damage | [7 empty] | D | 4
HAZ-CR-001 | HAZARD |  | CRH Steam | Condensate in CRH Steam | Fluid: condensate Location: CRH Steam
TE-CR-001 | TOP_EVENT | HAZ-CR-001 | CRH Steam | Loss of containment of cold reheat steam | Loss of containment of cold reheat steam
THR-CR-001 | THREAT | TE-CR-001 | CRH Steam | Equipment failure | Equipment failure
PB-CR-003 | PREVENTION | THR-CR-001 | CRH Steam | VALVE-10LBC01-AA402: Valve position feedback | VALVE-10LBC01-AA402: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 91 VALVE-10LBC01-AA402 S=4.
PB-CR-002 | PREVENTION | THR-CR-001 | CRH Steam | MOV-12LBC01-AA410: Motor operated isolation valve | MOV-12LBC01-AA410: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 87 MOV-12LBC01-AA410 S=4.
PB-CR-001 | PREVENTION | THR-CR-001 | CRH Steam | MOV-11LBC01-AA001: Motor operated isolation valve | MOV-11LBC01-AA001: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 80 MOV-11LBC01-AA001 S=4.
PB-AC-018-X-CD | PREVENTION | THR-CR-001 | CRH Steam | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2) | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 3623 FAL-10LCA04-CF101A/B S=4. Also protects ACC (PB-AC-018).
MB-CR-003 | MITIGATION | TE-CR-001 | CRH Steam | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-CR-001 | MITIGATION | TE-CR-001 | CRH Steam | Drain routing to safe location | Drain routing to safe location | Hardware - Passive | MI Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 521 for pressure-relieving and depressuring systems; drain disposal to a safe location per the design basis. Not in HAZOP; requires site validation. Ref: API 521.
MB-CR-002 | MITIGATION | TE-CR-001 | CRH Steam | Access restriction | Access restriction | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-CR-001 | CONSEQUENCE | TE-CR-001 | CRH Steam | 1. Increase in turbine exhaust temperature beyond acceptable limit. | 1. Increase in turbine exhaust temperature beyond acceptable limit. | [7 empty] | D | 4
CON-CR-002 | CONSEQUENCE | TE-CR-001 | CRH Steam | 1. Fail to drain from respective upstream location leading to accumulation of condensate and subsequent carryover to HRH damage. | 1. Fail to drain from respective upstream location leading to accumulation of condensate and subsequent carryover to HRH damage. | [7 empty] | D | 4
CON-CR-003 | CONSEQUENCE | TE-CR-001 | CRH Steam | 1. Over pressurization beyond acceptable limit of respective HRSG CRH section (HRSG tripped). | 1. Over pressurization beyond acceptable limit of respective HRSG CRH section (HRSG tripped). | [7 empty] | D | 4
HAZ-HH-001 | HAZARD |  | HRH Steam | Steam in HRH Steam | Fluid: steam Location: HRH Steam
TE-HH-001 | TOP_EVENT | HAZ-HH-001 | HRH Steam | Loss of containment of hot reheat steam | Loss of containment of hot reheat steam
THR-HH-001 | THREAT | TE-HH-001 | HRH Steam | Initiating event | Initiating event
PB-HH-006 | PREVENTION | THR-HH-001 | HRH Steam | Positive isolation (energy isolation for maintenance) | Positive isolation (energy isolation for maintenance) | Organizational | HSSE | EFFECTIVE |  |  | From HAZOP | Verified rows 162 S=4.
PB-HH-008 | PREVENTION | THR-HH-001 | HRH Steam | Online sampling of water / steam | Online sampling of water / steam | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 182 S=4.
PB-HH-007 | PREVENTION | THR-HH-001 | HRH Steam | LABLE11LBB10-CT123: Temperature elements are avai A/B/C to generate high | LABLE11LBB10-CT123: Temperature elements are avai A/B/C to generate high | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 179 LABLE11LBB10-CT123 S=4.
PB-HH-003 | PREVENTION | THR-HH-001 | HRH Steam | PAH-10LBB01-CP121A/B: Pressure alarm high (1oo2)and PAL-10LBB01-CP122 is | PAH-10LBB01-CP121A/B: Pressure alarm high (1oo2)and PAL-10LBB01-CP122 is | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 134 PAH-10LBB01-CP121A/B S=4.
PB-HH-001 | PREVENTION | THR-HH-001 | HRH Steam | FAL-11LBB10-CF121A/B: Flow alarm low (1oo2) | FAL-11LBB10-CF121A/B: Flow alarm low (1oo2) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 113 FAL-11LBB10-CF121A/B S=4.
THR-HH-002 | THREAT | TE-HH-001 | HRH Steam | Equipment failure | Equipment failure
PB-HH-005 | PREVENTION | THR-HH-002 | HRH Steam | FOR10LBB01-AA412: Valve position feedback | FOR10LBB01-AA412: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 157 FOR10LBB01-AA412 S=4.
PB-HH-004 | PREVENTION | THR-HH-002 | HRH Steam | VALVE-11LBB01-AA101: Valve position feedback | VALVE-11LBB01-AA101: Valve position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 144 VALVE-11LBB01-AA101 S=4.
PB-HH-002 | PREVENTION | THR-HH-002 | HRH Steam | MOV: Motor operated isolation valve | MOV: Motor operated isolation valve | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 118 S=4.
MB-HH-001 | MITIGATION | TE-HH-001 | HRH Steam | Steam leak detection and alarm | Steam leak detection and alarm | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 61511 SIF design for steam leak scenarios; detector placement per OEM recommendation. Not in HAZOP; requires site validation. Ref: IEC 61511, OEM O&M manual.
MB-HH-003 | MITIGATION | TE-HH-001 | HRH Steam | Emergency isolation (remote operated) | Emergency isolation (remote operated) | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per API 6D valve specification and IEC 61511 SIS design for remote-operated ESD. Not in HAZOP; requires site validation. Ref: API 6D, IEC 61511.
MB-HH-005 | MITIGATION | TE-HH-001 | HRH Steam | Insulation and lagging for personnel protection | Insulation and lagging for personnel protection | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-HH-004 | MITIGATION | TE-HH-001 | HRH Steam | Emergency operating procedures | Emergency operating procedures | Procedural | Operations | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per CCPS Guidelines for Risk Based Process Safety, Element 10 (Operating Procedures). Not in HAZOP; requires site validation. Ref: CCPS RBPS Ch.10, ISO 45001 S8.1.
MB-HH-002 | MITIGATION | TE-HH-001 | HRH Steam | Access restriction and exclusion zones | Access restriction and exclusion zones | Organizational | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per site safety management system; exclusion zone policy for MAH areas. Not in HAZOP; requires site validation. Ref: ISO 45001 S8.1, site SMS.
CON-HH-001 | CONSEQUENCE | TE-HH-001 | HRH Steam | 1. Lower power generation from steam turbine. | 1. Lower power generation from steam turbine. | [7 empty] | C | 3
CON-HH-002 | CONSEQUENCE | TE-HH-001 | HRH Steam | 1. Potential pressurization of upstream header of respective MOV resulting in damage. | 1. Potential pressurization of upstream header of respective MOV resulting in damage. | [7 empty] | D | 4
CON-HH-003 | CONSEQUENCE | TE-HH-001 | HRH Steam | 1. Potential for reverse flow of HRH steam from common header to HRSG under maintenance and subsequent human injury. | 1. Potential for reverse flow of HRH steam from common header to HRSG under maintenance and subsequent human injury. | [7 empty] | D | 4
CON-HH-004 | CONSEQUENCE | TE-HH-001 | HRH Steam | 1. Potential overheating of piping and turbine. | 1. Potential overheating of piping and turbine. | [7 empty] | D | 4
CON-HH-005 | CONSEQUENCE | TE-HH-001 | HRH Steam | 1. Substandard steam quality leading to turbine internal damage, inefficient functioning of turbine, enhance corrosion in turbine/piping. | 1. Substandard steam quality leading to turbine internal damage, inefficient functioning of turbine, enhance corrosion in turbine/piping. | [7 empty] | C | 3
HAZ-SL-001 | HAZARD |  | STG Seals | Hydrogen in STG Seals | Fluid: hydrogen Location: STG Seals
TE-SL-001 | TOP_EVENT | HAZ-SL-001 | STG Seals | Loss of containment from turbine shaft seals | Loss of containment from turbine shaft seals
THR-SL-001 | THREAT | TE-SL-001 | STG Seals | Initiating event | Initiating event
PB-SL-014 | PREVENTION | THR-SL-001 | STG Seals | LAH-10MKW01-CL101: Level alarm high (alert the operator) | LAH-10MKW01-CL101: Level alarm high (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2521 LAH-10MKW01-CL101 S=5.
PB-SL-013 | PREVENTION | THR-SL-001 | STG Seals | ECTOR10MKW21-BZ001: SODE will overflow to liquid det and alert the operator | ECTOR10MKW21-BZ001: SODE will overflow to liquid det and alert the operator | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2518 ECTOR10MKW21-BZ001 S=5.
PB-SL-012 | PREVENTION | THR-SL-001 | STG Seals | PSL10MKG21-CP101: alert the operator | PSL10MKG21-CP101: alert the operator | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2513 PSL10MKG21-CP101 S=5. Also protects Generator H2 (PSL10MKG21-CP101).
PB-SL-011 | PREVENTION | THR-SL-001 | STG Seals | Pump discharge line is designed for pump shut-off head. | Pump discharge line is designed for pump shut-off head. | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2503 S=5.
PB-SL-010 | PREVENTION | THR-SL-001 | STG Seals | FAL-10MKW06-CF001: Flow alarm low (alert the operator) | FAL-10MKW06-CF001: Flow alarm low (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2488 FAL-10MKW06-CF001 S=5.
PB-SL-009 | PREVENTION | THR-SL-001 | STG Seals | PDAH-10MKW10-CP001: Differential pressure alarm high (A/B (1oo) | PDAH-10MKW10-CP001: Differential pressure alarm high (A/B (1oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2485 PDAH-10MKW10-CP001 S=5.
THR-SL-002 | THREAT | TE-SL-001 | STG Seals | Equipment failure | Equipment failure
PB-SL-004 | PREVENTION | THR-SL-002 | STG Seals | Auto start of standby Gland condenser blower on tripping of duty blower. | Auto start of standby Gland condenser blower on tripping of duty blower. | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2149 S=5.
PB-SL-002 | PREVENTION | THR-SL-002 | STG Seals | PCV: Pressure control valve (Field positioner / Discrepancy position feedback | PCV: Pressure control valve (Field positioner / Discrepancy position feedback | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2126 S=5.
MB-SL-001 | MITIGATION | TE-SL-001 | STG Seals | H2-specific catalytic detector | H2-specific catalytic detector | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 60079-29-1 for hydrogen detection; catalytic/electrochemical sensor selection per EN 50073. Not in HAZOP; requires site validation. Ref: IEC 60079-29-1, EN 50073.
MB-SL-002 | MITIGATION | TE-SL-001 | STG Seals | Ventilation system with gas interlock | Ventilation system with gas interlock | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per IEC 60079-10-1 for ventilation in hazardous areas; air change rate per ATEX assessment. Not in HAZOP; requires site validation. Ref: IEC 60079-10-1, ATEX directive.
MB-SL-003 | MITIGATION | TE-SL-001 | STG Seals | Explosion relief panels | Explosion relief panels | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-SL-004 | MITIGATION | TE-SL-001 | STG Seals | Blast-rated generator building (API 752) | Blast-rated generator building (API 752) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-SL-005 | MITIGATION | TE-SL-001 | STG Seals | Hazardous area classification (IEC 60079) | Hazardous area classification (IEC 60079) | Hardware - Passive | MI Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-SL-001 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Fail to hold seal for HP/IP/LP turbine leading to entry of non-condensable gasses on steam side further leading to vacuum and performance reduction. | 1. Fail to hold seal for HP/IP/LP turbine leading to entry of non-condensable gasses on steam side further leading to vacuum and performance reduction. | [7 empty] | C | 3
CON-SL-002 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Potential steam leakage from the turbine side leading to contamination of Lube oil leading to deterioration of bearings performance over a period of time. | 1. Potential steam leakage from the turbine side leading to contamination of Lube oil leading to deterioration of bearings performance over a period of time. | [7 empty] | E | 5
CON-SL-003 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Potential for high temperature steam supply to LP turbine seal and subsequent seal damage and contamination of lube oil system. | 1. Potential for high temperature steam supply to LP turbine seal and subsequent seal damage and contamination of lube oil system. | [7 empty] | D | 4
CON-SL-004 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Potential for condensate entry to Shell side leading to deterioration of vacuum and subsequent process upset | 1. Potential for condensate entry to Shell side leading to deterioration of vacuum and subsequent process upset | [7 empty] | E | 5
CON-SL-005 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Loss of seal oil circulation to generator T&C end and subsequent bearing damage. | 1. Loss of seal oil circulation to generator T&C end and subsequent bearing damage. | [7 empty] | C | 3
CON-SL-006 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Potential high pressure in seal oil circuit. However not significant. | 1. Potential high pressure in seal oil circuit. However not significant. | [7 empty] | C | 3
CON-SL-007 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Potential loss of seal oil to generator leading to hydrogen seal breakage. | 1. Potential loss of seal oil to generator leading to hydrogen seal breakage. | [7 empty] | C | 3
CON-SL-008 | CONSEQUENCE | TE-SL-001 | STG Seals | 1. Potential level build up in SODE and subsequent seal oil entering inside the generator. | 1. Potential level build up in SODE and subsequent seal oil entering inside the generator. | [7 empty] | D | 4
HAZ-LO-001 | HAZARD |  | STG Lube Oil | Lube oil in STG Lube Oil | Fluid: lube oil Location: STG Lube Oil
TE-LO-001 | TOP_EVENT | HAZ-LO-001 | STG Lube Oil | Loss of containment of lube oil from ST system | Loss of containment of lube oil from ST system
THR-LO-001 | THREAT | TE-LO-001 | STG Lube Oil | Equipment failure | Equipment failure
PB-LO-005 | PREVENTION | THR-LO-001 | STG Lube Oil | Turn around PM schedule is available | Turn around PM schedule is available | Procedural | Operations | EFFECTIVE |  |  | From HAZOP | Verified rows 2359 S=4.
PB-LO-004 | PREVENTION | THR-LO-001 | STG Lube Oil | TAH-10MAV95-CT122: Temperature alarm high (A/B (1oo) | TAH-10MAV95-CT122: Temperature alarm high (A/B (1oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2340 TAH-10MAV95-CT122 S=4.
PB-LO-003 | PREVENTION | THR-LO-001 | STG Lube Oil | PAH-10MAV95-CP125: Pressure alarm high (A/B/C (2oo) | PAH-10MAV95-CP125: Pressure alarm high (A/B/C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2328 PAH-10MAV95-CP125 S=4.
PB-LO-002 | PREVENTION | THR-LO-001 | STG Lube Oil | PDAH-10MAV93-CP181: Differential pressure alarm high (alert the operator) | PDAH-10MAV93-CP181: Differential pressure alarm high (alert the operator) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2308 PDAH-10MAV93-CP181 S=4.
PB-LO-001 | PREVENTION | THR-LO-001 | STG Lube Oil | PAL-10MAV95-CP125: Pressure alarm low (A/B/C (2oo) | PAL-10MAV95-CP125: Pressure alarm low (A/B/C (2oo) | Hardware - Active | I&C Eng | EFFECTIVE |  |  | From HAZOP | Verified rows 2302 PAL-10MAV95-CP125 S=4.
THR-LO-002 | THREAT | TE-LO-001 | STG Lube Oil | Initiating event | Initiating event
MB-LO-001 | MITIGATION | TE-LO-001 | STG Lube Oil | Oil mist detection | Oil mist detection | Hardware - Active | I&C Eng | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per OEM recommendation for turbine enclosure; oil mist concentration alarm per machine protection. Not in HAZOP; requires site validation. Ref: OEM O&M manual, API 670.
MB-LO-002 | MITIGATION | TE-LO-001 | STG Lube Oil | CO2 / clean agent fire suppression | CO2 / clean agent fire suppression | Hardware - Active | I&C Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-LO-004 | MITIGATION | TE-LO-001 | STG Lube Oil | Flame detection near hot surfaces | Flame detection near hot surfaces | Hardware - Active | HSSE | PARTIALLY_EFFECTIVE |  |  | Domain knowledge | Per NFPA 72 for flame detector selection; UV/IR technology per EN 54-10. Not in HAZOP; requires site validation. Ref: NFPA 72, EN 54-10.
MB-LO-003 | MITIGATION | TE-LO-001 | STG Lube Oil | Drip trays and bund containment | Drip trays and bund containment | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
MB-LO-005 | MITIGATION | TE-LO-001 | STG Lube Oil | Fireproofing on structural steel (UL 1709) | Fireproofing on structural steel (UL 1709) | Hardware - Passive | Project Eng | EFFECTIVE |  |  | Engineering standard | Design basis per industry standard referenced in title. Not a HAZOP safeguard.
CON-LO-001 | CONSEQUENCE | TE-LO-001 | STG Lube Oil | 1. Loss of lube oil supply leading to turbine bearing damage | 1. Loss of lube oil supply leading to turbine bearing damage | [7 empty] | D | 4

## Threat-Consequence Links
Link ID | System | Threat ID | Threat Title | Consequence ID | Consequence Title | Severity
L-AC-001-01 | ACC | THR-AC-001 | Tube leak from corrosion or mechanical damage | CON-AC-002 | Steam release causing equipment damage | 4
L-AC-001-02 | ACC | THR-AC-002 | Vacuum system failure causing air ingress | CON-AC-002 | Steam release causing equipment damage | 4
L-AX-001-03 | Auxiliary Steam | THR-AX-001 | Aux steam line leak at flanged connection | CON-AX-001 | Aux steam leak / scald | 3
L-AX-001-04 | Auxiliary Steam | THR-AX-002 | Pressure excursion from PRV failure | CON-AX-001 | Aux steam leak / scald | 3
L-BY-001-05 | HRSG Bypass | THR-BY-001 | Bypass valve failure to open on turbine trip | CON-BY-001 | Steam jet injury to personnel | 4
L-BY-001-06 | HRSG Bypass | THR-BY-002 | Steam release from bypass valve body/bonnet leak | CON-BY-001 | Steam jet injury to personnel | 4
L-DB-001-07 | HRSG Duct Burner | THR-DB-001 | Uncontrolled gas release from duct burner supply | CON-DB-001 | Jet fire | 5
L-DB-001-08 | HRSG Duct Burner | THR-DB-001 | Uncontrolled gas release from duct burner supply | CON-DB-002 | Vapour cloud explosion | 5
L-DB-001-09 | HRSG Duct Burner | THR-DB-001 | Uncontrolled gas release from duct burner supply | CON-DB-003 | Flash fire | 4
L-DB-001-10 | HRSG Duct Burner | THR-DB-002 | Flame failure with delayed re-ignition attempt | CON-DB-001 | Jet fire | 5
L-FG-001-11 | Fuel Gas | THR-FG-001 | Overpressure due to regulator failure or blocked outlet | CON-FG-001 | Vapour cloud explosion in congested area | 5
L-FG-001-12 | Fuel Gas | THR-FG-001 | Overpressure due to regulator failure or blocked outlet | CON-FG-002 | Equipment damage requiring forced outage | 4
L-FG-001-13 | Fuel Gas | THR-FG-002 | External corrosion / mechanical damage to pipework | CON-FG-001 | Vapour cloud explosion in congested area | 5
L-FG-001-14 | Fuel Gas | THR-FG-002 | External corrosion / mechanical damage to pipework | CON-FG-002 | Equipment damage requiring forced outage | 4
L-FG-001-15 | Fuel Gas | THR-FG-003 | Flange or connection leak (vibration / thermal cycling) | CON-FG-001 | Vapour cloud explosion in congested area | 5
L-FG-001-16 | Fuel Gas | THR-FG-003 | Flange or connection leak (vibration / thermal cycling) | CON-FG-002 | Equipment damage requiring forced outage | 4
L-FG-001-17 | Fuel Gas | THR-FG-004 | Valve passing during maintenance or isolation | CON-FG-001 | Vapour cloud explosion in congested area | 5
L-FG-001-18 | Fuel Gas | THR-FG-004 | Valve passing during maintenance or isolation | CON-FG-002 | Equipment damage requiring forced outage | 4
L-FO-001-19 | Fuel Oil | THR-FO-001 | Flange leak from fuel oil pipework | CON-FO-001 | Jet fire | 5
L-FO-001-20 | Fuel Oil | THR-FO-001 | Flange leak from fuel oil pipework | CON-FO-002 | Vapour cloud explosion | 5
L-FO-001-21 | Fuel Oil | THR-FO-001 | Flange leak from fuel oil pipework | CON-FO-003 | Flash fire | 4
L-FO-001-22 | Fuel Oil | THR-FO-002 | Tank overflow or overfill during delivery | CON-FO-001 | Jet fire | 5
L-FO-001-23 | Fuel Oil | THR-FO-003 | Pump seal failure | CON-FO-001 | Jet fire | 5
L-FW-001-24 | Feedwater | THR-FW-001 | BFP discharge pipe rupture (high energy) | CON-FW-001 | Pipe rupture and equipment damage | 3
L-FW-001-25 | Feedwater | THR-FW-002 | Feedwater chemistry excursion causing tube damage | CON-FW-001 | Pipe rupture and equipment damage | 3
L-GH-001-26 | Generator H2 | THR-GH-001 | Seal failure allowing H2 escape to atmosphere | CON-GH-001 | Hydrogen explosion in generator building | 5
L-GH-001-27 | Generator H2 | THR-GH-002 | H2 purity loss (air ingress into casing) | CON-GH-001 | Hydrogen explosion in generator building | 5
L-GH-001-28 | Generator H2 | THR-GH-003 | Overpressure from H2 supply regulator failure | CON-GH-001 | Hydrogen explosion in generator building | 5
L-HI-001-29 | HRSG IP | THR-HI-001 | IP section tube leak from FAC or corrosion | CON-HI-001 | Tube rupture and IP steam release | 4
L-HI-001-30 | HRSG IP | THR-HI-001 | IP section tube leak from FAC or corrosion | CON-HI-002 | Major equipment failure with escalation potential | 5
L-HI-001-31 | HRSG IP | THR-HI-002 | Thermal stress during startup/shutdown transitions | CON-HI-001 | Tube rupture and IP steam release | 4
L-HL-001-32 | HRSG LP | THR-HL-001 | LP tube leak from FAC or corrosion | CON-HL-001 | LP steam release (scald hazard) | 3
L-HL-001-33 | HRSG LP | THR-HL-001 | LP tube leak from FAC or corrosion | CON-HL-002 | Major equipment failure with escalation potential | 5
L-HL-001-34 | HRSG LP | THR-HL-002 | Overpressure from stuck LP drum safety valve | CON-HL-001 | LP steam release (scald hazard) | 3
L-HL-001-35 | HRSG LP | THR-HL-002 | Overpressure from stuck LP drum safety valve | CON-HL-002 | Major equipment failure with escalation potential | 5
L-HP-001-36 | HP Steam | THR-HP-001 | Overpressure due to blocked outlet or regulator failure | CON-HP-002 | Pipe rupture and equipment damage | 4
L-HP-001-37 | HP Steam | THR-HP-002 | Condensate accumulation and water hammer | CON-HP-001 | Steam jet injury to personnel | 4
L-HP-001-38 | HP Steam | THR-HP-003 | Reverse flow during HRSG maintenance | CON-HP-001 | Steam jet injury to personnel | 4
L-HP-001-39 | HP Steam | THR-HP-003 | Reverse flow during HRSG maintenance | CON-HP-003 | Steam release causing equipment damage | 4
L-HP-001-40 | HP Steam | THR-HP-004 | Thermal overstress during startup/shutdown | CON-HP-001 | Steam jet injury to personnel | 4
L-HR-001-41 | HRSG HP | THR-HR-001 | Tube failure (creep / FAC / corrosion) | CON-HR-001 | HRSG casing damage / tube failure | 4
L-HR-001-42 | HRSG HP | THR-HR-002 | Feedwater chemistry excursion (caustic/acid attack) | CON-HR-001 | HRSG casing damage / tube failure | 4
L-HR-001-43 | HRSG HP | THR-HR-003 | Thermal stress during startup/shutdown transitions | CON-HR-001 | HRSG casing damage / tube failure | 4
L-HR-001-44 | HRSG HP | THR-HR-004 | Overpressure from blocked safety valve or stuck bypass | CON-HR-001 | HRSG casing damage / tube failure | 4
L-HR-001-45 | HRSG HP | THR-HR-004 | Overpressure from blocked safety valve or stuck bypass | CON-HR-002 | HP steam release internal to HRSG casing | 4
L-LP-001-46 | LP Steam | THR-LP-001 | LP steam line leak at flanged connection | CON-LP-001 | LP steam leak / scald | 3
L-LP-001-47 | LP Steam | THR-LP-001 | LP steam line leak at flanged connection | CON-LP-002 | Steam release causing equipment damage | 4
L-LP-001-48 | LP Steam | THR-LP-002 | LP PRV failure to reseat after overpressure event | CON-LP-001 | LP steam leak / scald | 3
L-NH-001-49 | Ammonia/SCR | THR-NH-001 | Transfer hose failure during unloading | CON-NH-001 | Toxic ammonia vapour cloud | 4
L-NH-001-50 | Ammonia/SCR | THR-NH-002 | Pipework leak in ammonia distribution system | CON-NH-001 | Toxic ammonia vapour cloud | 4
L-NH-001-51 | Ammonia/SCR | THR-NH-003 | Tank overfill or overpressure | CON-NH-001 | Toxic ammonia vapour cloud | 4
L-SS-001-52 | STG Steam | THR-SS-001 | HP/IP/LP steam leak at turbine casing joint | CON-SS-001 | Steam jet injury | 4
L-SS-001-53 | STG Steam | THR-SS-001 | HP/IP/LP steam leak at turbine casing joint | CON-SS-002 | Turbine damage | 4
L-SS-001-54 | STG Steam | THR-SS-001 | HP/IP/LP steam leak at turbine casing joint | CON-SS-003 | Steam release causing equipment damage | 4
L-SS-001-55 | STG Steam | THR-SS-002 | Gland steam system failure causing external leak | CON-SS-002 | Turbine damage | 4
L-SS-001-56 | STG Steam | THR-SS-003 | Valve stem leak on extraction or admission valves | CON-SS-001 | Steam jet injury | 4
L-SS-001-57 | STG Steam | THR-SS-003 | Valve stem leak on extraction or admission valves | CON-SS-002 | Turbine damage | 4
L-SS-001-58 | STG Steam | THR-SS-003 | Valve stem leak on extraction or admission valves | CON-SS-003 | Steam release causing equipment damage | 4
L-CR-001-59 | CRH Steam | THR-CR-001 | Equipment failure | CON-CR-001 | 1. Increase in turbine exhaust temperature beyond acceptable limit. | 4
L-CR-001-60 | CRH Steam | THR-CR-001 | Equipment failure | CON-CR-002 | 1. Fail to drain from respective upstream location leading to accumulation of condensate and subsequent carryover to HRH damage. | 4
L-CR-001-61 | CRH Steam | THR-CR-001 | Equipment failure | CON-CR-003 | 1. Over pressurization beyond acceptable limit of respective HRSG CRH section (HRSG tripped). | 4
L-HH-001-62 | HRH Steam | THR-HH-001 | Initiating event | CON-HH-001 | 1. Lower power generation from steam turbine. | 3
L-HH-001-63 | HRH Steam | THR-HH-001 | Initiating event | CON-HH-002 | 1. Potential pressurization of upstream header of respective MOV resulting in damage. | 4
L-HH-001-64 | HRH Steam | THR-HH-001 | Initiating event | CON-HH-003 | 1. Potential for reverse flow of HRH steam from common header to HRSG under maintenance and subsequent human injury. | 4
L-HH-001-65 | HRH Steam | THR-HH-001 | Initiating event | CON-HH-004 | 1. Potential overheating of piping and turbine. | 4
L-HH-001-66 | HRH Steam | THR-HH-001 | Initiating event | CON-HH-005 | 1. Substandard steam quality leading to turbine internal damage, inefficient functioning of turbine, enhance corrosion in turbine/piping. | 3
L-HH-001-67 | HRH Steam | THR-HH-002 | Equipment failure | CON-HH-002 | 1. Potential pressurization of upstream header of respective MOV resulting in damage. | 4
L-SL-001-68 | STG Seals | THR-SL-001 | Initiating event | CON-SL-001 | 1. Fail to hold seal for HP/IP/LP turbine leading to entry of non-condensable gasses on steam side further leading to vacuum and performance reduction. | 3
L-SL-001-69 | STG Seals | THR-SL-001 | Initiating event | CON-SL-004 | 1. Potential for condensate entry to Shell side leading to deterioration of vacuum and subsequent process upset | 5
L-SL-001-70 | STG Seals | THR-SL-001 | Initiating event | CON-SL-005 | 1. Loss of seal oil circulation to generator T&C end and subsequent bearing damage. | 3
L-SL-001-71 | STG Seals | THR-SL-001 | Initiating event | CON-SL-007 | 1. Potential loss of seal oil to generator leading to hydrogen seal breakage. | 3
L-SL-001-72 | STG Seals | THR-SL-001 | Initiating event | CON-SL-008 | 1. Potential level build up in SODE and subsequent seal oil entering inside the generator. | 4
L-SL-001-73 | STG Seals | THR-SL-002 | Equipment failure | CON-SL-001 | 1. Fail to hold seal for HP/IP/LP turbine leading to entry of non-condensable gasses on steam side further leading to vacuum and performance reduction. | 3
L-SL-001-74 | STG Seals | THR-SL-002 | Equipment failure | CON-SL-002 | 1. Potential steam leakage from the turbine side leading to contamination of Lube oil leading to deterioration of bearings performance over a period of time. | 5
L-SL-001-75 | STG Seals | THR-SL-002 | Equipment failure | CON-SL-003 | 1. Potential for high temperature steam supply to LP turbine seal and subsequent seal damage and contamination of lube oil system. | 4
L-SL-001-76 | STG Seals | THR-SL-002 | Equipment failure | CON-SL-006 | 1. Potential high pressure in seal oil circuit. However not significant. | 3
L-SL-001-77 | STG Seals | THR-SL-002 | Equipment failure | CON-SL-007 | 1. Potential loss of seal oil to generator leading to hydrogen seal breakage. | 3
L-LO-001-78 | STG Lube Oil | THR-LO-001 | Equipment failure | CON-LO-001 | 1. Loss of lube oil supply leading to turbine bearing damage | 4
L-LO-001-79 | STG Lube Oil | THR-LO-002 | Initiating event | CON-LO-001 | 1. Loss of lube oil supply leading to turbine bearing damage | 4

## Gap Analysis
Finding ID | Priority | System | Gap Type | Affected Pathway | Current State | Required State | Recommendation | Action Owner | Target
F-001 | CRITICAL | ACC | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-SCOPE-001 | CRITICAL | Cross-cutting (all systems) | Incomplete asset-level HAZOP coverage | All pathways | Submitted HAZOP covers 10 of 32 mandatory systems for CCGT scope (31%). Classification: LIMITED. | Complete Combined Cycle Gas Turbine asset-level HAZOP coverage per Ascendera Thermal Power Reference Scope v1.0, with all 32 mandatory systems for this variant covered by HAZOP deviations, causes, consequences, and safeguards. Reference: IEC 61882:2016 Cl. 5.3.3, IFC Performance Standards, IFC EHS Thermal Power 2008, NFPA 850 for electric generating stations, and variant-specific standards from the reference scope. | Extend HAZOP scope to cover the missing mandatory systems: Fuel Gas Receiving Station, Gas Turbine Lubrication System, GT Enclosure Ventilation and Fire Suppression, HRSG Drums (HP/IP/LP) and Downcomer System, Superheater and Reheater, Economiser, Steam Turbine Lube, Seal, and Control Oil, Condensate Polishing, Demineralisation Water Treatment, Boiler Water Chemical Dosing, Generator Step-Up Transformer, Unit Auxiliary and Station Service Transformers, HV / EHV Switchyard (AIS or GIS), Medium Voltage Switchgear, Emergency Diesel Generator, Distributed Control System and SCADA, Safety Instrumented System / Emergency Shutdown, Fire and Gas Detection, Special Hazard Fire Suppression, Plant Service Air, Nitrogen Generation and Distribution, HVAC for MCC, Chemical Buildings, Control Room. | Process Safety Lead | 60 days
F-002 | CRITICAL | Auxiliary Steam | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-003 | CRITICAL | HRSG Bypass | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-004 | CRITICAL | CRH Steam | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 3 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-005 | CRITICAL | HRSG Duct Burner | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 7 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-006 | CRITICAL | HRSG Duct Burner | Missing mitigation barriers | PB-DB-002 | Single barrier on domain_knowledge pathway (THR-DB-002). Single point of failure on S=5 catastrophic consequence. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-007 | CRITICAL | Fuel Gas | Missing mitigation barriers | PB-FG-029 | Single barrier on from_hazop pathway (THR-FG-002). Single point of failure on S=5 catastrophic consequence. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-008 | CRITICAL | Fuel Oil | Missing mitigation barriers | All pathways | Flange and connection leaks on lube oil pipework are caused by vibration-induced bolt relaxation, gasket degradation, and thermal cycling. Standard prevention includes: joint integrity management programme (ASME PCC-1), controlled bolt torquing procedures, vibration monitoring on turbine/generator bearings, and periodic inspection of flange connections during planned outages. The HAZOP did not document joint integrity or inspection safeguards for lube oil flanges. Verify: (a) joint integrity programme scope covers lube oil system, (b) bolt torque records for critical flanges, (c) vibration trending data, (d) flange inspection scope in planned maintenance. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-009 | CRITICAL | Fuel Oil | Missing mitigation barriers | All pathways | Tank overflow during fuel oil delivery is prevented by independent high-level alarms (LAH), high-high level trips (LAHH) with automatic shutoff of the transfer pump or inlet valve, and secondary containment (bund) sized to contain the full tank volume plus rainfall. The HAZOP did not document level protection or overflow prevention for the fuel oil storage tank as safeguards. Verify: (a) independent LAH and LAHH instruments on the tank, (b) automatic transfer pump trip on LAHH, (c) bund sizing and drainage arrangement, (d) delivery procedure with operator attendance requirements. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-010 | CRITICAL | Fuel Oil | Missing mitigation barriers | All pathways | Pump seal failure on fuel oil transfer or forwarding pumps releases flammable liquid at the pump skid. Standard prevention includes: dual mechanical seals (API Plan 52/54), seal flush systems, bearing temperature and vibration monitoring with alarm and trip, and seal leak detection (drip collection, level alarm on seal drain pot). The HAZOP did not list seal-specific safeguards for fuel oil pumps. Verify: (a) seal arrangement type (single/dual/tandem), (b) seal support system (flush, quench, buffer), (c) seal leak detection method, (d) bearing monitoring with trip setpoints. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-011 | CRITICAL | Feedwater | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 4 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-012 | CRITICAL | Generator H2 | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-013 | CRITICAL | Generator H2 | Missing mitigation barriers | All pathways | Vacuum system failure in the ACC allows air ingress into the steam space, degrading condenser performance and potentially causing oxygen corrosion of tube internals. This mechanism is typically prevented by vacuum pump redundancy, air ejector systems, and vacuum leak detection. The HAZOP documented safeguards for tube leak and pressure control but did not address the vacuum-loss initiation mechanism as a separate cause. Verify: (a) vacuum pump standby/auto-start arrangement, (b) vacuum alarm setpoints and operator response procedure, (c) air ingress detection (e.g., dissolved oxygen monitoring). | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-014 | CRITICAL | HRH Steam | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-015 | CRITICAL | HRSG IP | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-016 | CRITICAL | HRSG IP | Missing mitigation barriers | All pathways | Thermal stress during startup/shutdown transitions is a primary damage mechanism for HRSG tubes, headers, and drums. Rapid temperature changes cause differential expansion between thick-walled components (drums, headers) and thin-walled tubes, leading to fatigue cracking at welds and penetrations. Standard prevention includes: controlled ramp rates per OEM limits (typically 2-5 deg C/min for drums), metal temperature monitoring at critical locations, hold periods for thermal soaking, cascaded bypass warming sequences, and automated GT load-hold interlocks tied to HRSG metal temperatures. The HAZOP documented hardware alarms but did not capture the startup SOP and ramp-rate controls as safeguards. Verify: (a) OEM ramp rate limits in the DCS, (b) startup SOP including hold-point criteria, (c) metal temperature monitoring locations and alarm setpoints, (d) cyclic life expenditure (CLE) tracking system. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-017 | CRITICAL | HRSG LP | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-018 | CRITICAL | HP Steam | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-019 | CRITICAL | HRSG HP | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-020 | CRITICAL | STG Lube Oil | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-021 | CRITICAL | LP Steam | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-022 | CRITICAL | Ammonia/SCR | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 6 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-023 | CRITICAL | STG Seals | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-024 | CRITICAL | STG Steam | Missing mitigation barriers | All pathways | No mitigative barriers identified in HAZOP. All 5 suggested barriers marked for validation. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Process Safety Lead | 60 days
F-025 | MAJOR | ACC | Single barrier / over-reliance | All pathways | Vacuum system failure in the ACC allows air ingress into the steam space, degrading condenser performance and potentially causing oxygen corrosion of tube internals. This mechanism is typically prevented by vacuum pump redundancy, air ejector systems, and vacuum leak detection. The HAZOP documented safeguards for tube leak and pressure control but did not address the vacuum-loss initiation mechanism as a separate cause. Verify: (a) vacuum pump standby/auto-start arrangement, (b) vacuum alarm setpoints and operator response procedure, (c) air ingress detection (e.g., dissolved oxygen monitoring). | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-SYS-001 | MAJOR | Cross-cutting (all systems) | HAZOP methodology gap | All pathways | HAZOP methodology gap: the source HAZOP safeguard set is dominated by instrumented hardware barriers (alarms, trips, interlocks, valve position feedback). Of 39 human / procedural / organizational barriers in this assessment only 16 were extracted from HAZOP rows; the rest were added from domain knowledge and engineering standards. Emergency operating procedures, permit-to-work systems, pre-startup safety reviews, shift handover protocols, and management-of-change processes are not documented as HAZOP safeguards. Recommendation: run a supplementary workshop focused on non-hardware barriers so they are captured as HAZOP safeguards rather than tool inferences. Owner: Process Safety Lead. Target: 90 days. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Add human / procedural barriers (emergency procedures, permit-to-work, competency requirements) to the HAZOP. | Facility Owner | 90 days
F-SYS-002 | MAJOR | Cross-cutting (all systems) | Defence-in-depth diversity gap | All pathways | Defence-in-depth diversity gap: barrier type distribution across the assessment is Hardware-Active 73%, Hardware-Passive 10%, Procedural 10%, Organizational 6%, Human-Active 1%. Barrier ownership is concentrated: I&C Eng owns 65% of all barriers; Operations owns 11%. Per CCPS / EI each critical threat pathway should have barriers from at least two of three categories (Technical / Operational / Organizational). Conduct a barrier-diversity review with multi-discipline participation (Operations, Maintenance, HSE, I&C). Owner: HSSE Manager. Target: 90 days. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Run a multi-discipline barrier-diversity review so each pathway has both technical and operational defences. | Facility Owner | 90 days
F-026 | MAJOR | ACC | Common-cause failure vulnerability | All pathways | Common-cause failure vulnerability on ACC: 82% of barriers (9/11) are owned by I&C Eng. A systematic failure in that discipline's domain (DCS failure, instrument air loss, staffing gap) would simultaneously degrade the majority of barriers. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Assess common-cause failure modes for I&C Eng-owned barriers on ACC. Consider diversifying barrier ownership by adding operational or procedural layers. | Facility Owner | 90 days
F-027 | MAJOR | ACC | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on ACC: all 6 prevention barriers on 'Tube leak from corrosion or mechanical damage' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Tube leak from corrosion or mechanical damage' pathway on ACC. | Facility Owner | 90 days
F-028 | MAJOR | ACC | Shared barrier dependency | All pathways | Shared barrier dependency: 'Steam leak detection and alarm' appears in 10 of 19 systems (53%). Degradation of this single barrier simultaneously weakens protection across ACC, Auxiliary Steam, HP Steam, HRH Steam, HRSG Bypass.... This creates a systemic single-point-of-failure dependency. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Confirm 'Steam leak detection and alarm' is installed, tested, and maintained. Verify inclusion in the maintenance programme with appropriate test intervals. Consider redundancy or diversity given its criticality across 10 systems. | Facility Owner | 90 days
F-029 | MAJOR | ACC | Shared barrier dependency | All pathways | Shared barrier dependency: 'Emergency isolation (remote operated)' appears in 10 of 19 systems (53%). Degradation of this single barrier simultaneously weakens protection across ACC, Auxiliary Steam, HP Steam, HRH Steam, HRSG Bypass.... This creates a systemic single-point-of-failure dependency. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Confirm 'Emergency isolation (remote operated)' is installed, tested, and maintained. Verify inclusion in the maintenance programme with appropriate test intervals. Consider redundancy or diversity given its criticality across 10 systems. | Facility Owner | 90 days
F-030 | MAJOR | ACC | Shared barrier dependency | All pathways | Shared barrier dependency: 'Emergency operating procedures' appears in 10 of 19 systems (53%). Degradation of this single barrier simultaneously weakens protection across ACC, Auxiliary Steam, HP Steam, HRH Steam, HRSG Bypass.... This creates a systemic single-point-of-failure dependency. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Confirm 'Emergency operating procedures' is installed, tested, and maintained. Verify inclusion in the maintenance programme with appropriate test intervals. Consider redundancy or diversity given its criticality across 10 systems. | Facility Owner | 90 days
F-031 | MAJOR | ACC | Shared barrier dependency | All pathways | Shared barrier dependency: 'Access restriction and exclusion zones' appears in 10 of 19 systems (53%). Degradation of this single barrier simultaneously weakens protection across ACC, Auxiliary Steam, HP Steam, HRH Steam, HRSG Bypass.... This creates a systemic single-point-of-failure dependency. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Confirm 'Access restriction and exclusion zones' is installed, tested, and maintained. Verify inclusion in the maintenance programme with appropriate test intervals. Consider redundancy or diversity given its criticality across 10 systems. | Facility Owner | 90 days
F-032 | MAJOR | ACC | Shared barrier dependency | All pathways | Shared barrier dependency: 'Insulation and lagging for personnel protection' appears in 12 of 19 systems (63%). Degradation of this single barrier simultaneously weakens protection across ACC, Auxiliary Steam, CRH Steam, Feedwater, HP Steam.... This creates a systemic single-point-of-failure dependency. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Confirm 'Insulation and lagging for personnel protection' is installed, tested, and maintained. Verify inclusion in the maintenance programme with appropriate test intervals. Consider redundancy or diversity given its criticality across 12 systems. | Facility Owner | 90 days
F-033 | MAJOR | ACC | Shared barrier dependency | All pathways | Shared barrier dependency: 'Online sampling of water / steam' appears in 8 of 19 systems (42%). Degradation of this single barrier simultaneously weakens protection across Auxiliary Steam, Feedwater, HP Steam, HRH Steam, HRSG HP.... This creates a systemic single-point-of-failure dependency. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Confirm 'Online sampling of water / steam' is installed, tested, and maintained. Verify inclusion in the maintenance programme with appropriate test intervals. Consider redundancy or diversity given its criticality across 8 systems. | Facility Owner | 90 days
F-SCOPE-002 | MAJOR | Cross-cutting (all systems) | Variant not declared for thermal power scope | All pathways | Variant not declared on CLI; scope benchmark defaulted to natural gas CCGT. A hydrogen-ready, cogeneration, coal, biomass, waste-to-energy, or reciprocating plant has materially different mandatory scope and cannot be assessed accurately against the default. | Variant explicitly declared via --variant {ccgt¦ocgt¦cogen¦ccgt_h2¦pc¦cfb¦oil¦biomass¦efw¦recip} so the mandatory-system benchmark matches the plant architecture. | Re-run the pipeline with --variant set to the plant's actual technology variant, then review the updated scope completeness report. | Facility Owner | 90 days
F-034 | MAJOR | Auxiliary Steam | Single barrier / over-reliance | All pathways | PRV failure to reseat after a legitimate overpressure event causes continuous steam release until the system is depressurised and the PRV can be isolated for maintenance. This is a known failure mode where the valve lifts correctly but the seat is damaged by the high-velocity steam flow and cannot re-seal. Prevention includes: regular PRV bench testing (typically 12-month cycle per API 576), selection of resilient-seat designs for clean steam service, and installed-spare PRV arrangements allowing online changeover. The HAZOP did not list PRV testing or maintenance as a safeguard. Verify: (a) PRV test interval and compliance history, (b) PRV type and seat material, (c) spare PRV arrangement for online changeout. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-035 | MAJOR | HRSG Bypass | Single barrier / over-reliance | All pathways | Threat pathway 'Steam release from bypass valve body/bonnet leak' has zero prevention barriers. No HAZOP safeguard could be matched to this initiating event. Verify whether prevention barriers exist at the plant but were not documented in the HAZOP study. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-036 | MAJOR | HRSG Bypass | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on HRSG Bypass: all 3 prevention barriers on 'Bypass valve failure to open on turbine trip' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Bypass valve failure to open on turbine trip' pathway on HRSG Bypass. | Facility Owner | 90 days
F-037 | MAJOR | CRH Steam | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on CRH Steam: all 4 prevention barriers on 'Equipment failure' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Equipment failure' pathway on CRH Steam. | Facility Owner | 90 days
F-038 | MAJOR | Fuel Gas | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on Fuel Gas: all 3 prevention barriers on 'Flange or connection leak (vibration / thermal cycling)' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Flange or connection leak (vibration / thermal cycling)' pathway on Fuel Gas. | Facility Owner | 90 days
F-039 | MAJOR | Fuel Gas | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on Fuel Gas: all 6 prevention barriers on 'Valve passing during maintenance or isolation' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Valve passing during maintenance or isolation' pathway on Fuel Gas. | Facility Owner | 90 days
F-040 | MAJOR | Feedwater | Common-cause failure vulnerability | All pathways | Common-cause failure vulnerability on Feedwater: 77% of barriers (10/13) are owned by I&C Eng. A systematic failure in that discipline's domain (DCS failure, instrument air loss, staffing gap) would simultaneously degrade the majority of barriers. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Assess common-cause failure modes for I&C Eng-owned barriers on Feedwater. Consider diversifying barrier ownership by adding operational or procedural layers. | Facility Owner | 90 days
F-041 | MAJOR | Feedwater | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on Feedwater: all 3 prevention barriers on 'Feedwater chemistry excursion causing tube damage' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Feedwater chemistry excursion causing tube damage' pathway on Feedwater. | Facility Owner | 90 days
F-042 | MAJOR | Generator H2 | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on Generator H2: all 3 prevention barriers on 'Seal failure allowing H2 escape to atmosphere' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Seal failure allowing H2 escape to atmosphere' pathway on Generator H2. | Facility Owner | 90 days
F-043 | MAJOR | Generator H2 | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on Generator H2: all 2 prevention barriers on 'Overpressure from H2 supply regulator failure' are 'Hardware - Passive'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Overpressure from H2 supply regulator failure' pathway on Generator H2. | Facility Owner | 90 days
F-044 | MAJOR | HRH Steam | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on HRH Steam: all 3 prevention barriers on 'Equipment failure' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Equipment failure' pathway on HRH Steam. | Facility Owner | 90 days
F-045 | MAJOR | HP Steam | Single barrier / over-reliance | PB-HP-007 | Single barrier on from_hazop pathway (THR-HP-002). S=4 single-point-of-failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-046 | MAJOR | HP Steam | Single barrier / over-reliance | All pathways | Thermal stress during startup/shutdown transitions is a primary damage mechanism for HRSG tubes, headers, and drums. Rapid temperature changes cause differential expansion between thick-walled components (drums, headers) and thin-walled tubes, leading to fatigue cracking at welds and penetrations. Standard prevention includes: controlled ramp rates per OEM limits (typically 2-5 deg C/min for drums), metal temperature monitoring at critical locations, hold periods for thermal soaking, cascaded bypass warming sequences, and automated GT load-hold interlocks tied to HRSG metal temperatures. The HAZOP documented hardware alarms but did not capture the startup SOP and ramp-rate controls as safeguards. Verify: (a) OEM ramp rate limits in the DCS, (b) startup SOP including hold-point criteria, (c) metal temperature monitoring locations and alarm setpoints, (d) cyclic life expenditure (CLE) tracking system. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-047 | MAJOR | HRSG HP | Single barrier / over-reliance | All pathways | Threat pathway 'Feedwater chemistry excursion (caustic/acid attack)' has zero prevention barriers. No HAZOP safeguard could be matched to this initiating event. Verify whether prevention barriers exist at the plant but were not documented in the HAZOP study. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-048 | MAJOR | HRSG HP | Single barrier / over-reliance | All pathways | Thermal stress during startup/shutdown transitions is a primary damage mechanism for HRSG tubes, headers, and drums. Rapid temperature changes cause differential expansion between thick-walled components (drums, headers) and thin-walled tubes, leading to fatigue cracking at welds and penetrations. Standard prevention includes: controlled ramp rates per OEM limits (typically 2-5 deg C/min for drums), metal temperature monitoring at critical locations, hold periods for thermal soaking, cascaded bypass warming sequences, and automated GT load-hold interlocks tied to HRSG metal temperatures. The HAZOP documented hardware alarms but did not capture the startup SOP and ramp-rate controls as safeguards. Verify: (a) OEM ramp rate limits in the DCS, (b) startup SOP including hold-point criteria, (c) metal temperature monitoring locations and alarm setpoints, (d) cyclic life expenditure (CLE) tracking system. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-049 | MAJOR | HRSG HP | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on HRSG HP: all 6 prevention barriers on 'Overpressure from blocked safety valve or stuck bypass' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Overpressure from blocked safety valve or stuck bypass' pathway on HRSG HP. | Facility Owner | 90 days
F-050 | MAJOR | STG Lube Oil | Single barrier / over-reliance | All pathways | Threat pathway 'Initiating event' has zero prevention barriers. No HAZOP safeguard could be matched to this initiating event. Verify whether prevention barriers exist at the plant but were not documented in the HAZOP study. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-051 | MAJOR | LP Steam | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on LP Steam: all 2 prevention barriers on 'LP PRV failure to reseat after overpressure event' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'LP PRV failure to reseat after overpressure event' pathway on LP Steam. | Facility Owner | 90 days
F-052 | MAJOR | Ammonia/SCR | Single barrier / over-reliance | All pathways | Pipework leak in the ammonia distribution system releases toxic vapour. Aqueous ammonia (19-25%) has a significant vapour pressure and can produce a toxic cloud at ambient temperature. Standard prevention includes: corrosion-resistant material selection (typically SS316L or HDPE), flanged connection minimisation (welded construction preferred), periodic wall thickness measurement, and hazardous area classification around ammonia piping routes. The HAZOP documented transfer hose safeguards but did not address fixed pipework integrity. Verify: (a) piping material specification, (b) joint types (welded vs flanged), (c) inspection scope includes ammonia distribution piping, (d) leak detection coverage of ammonia pipe routes. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-053 | MAJOR | Ammonia/SCR | Single barrier / over-reliance | All pathways | Tank overflow during fuel oil delivery is prevented by independent high-level alarms (LAH), high-high level trips (LAHH) with automatic shutoff of the transfer pump or inlet valve, and secondary containment (bund) sized to contain the full tank volume plus rainfall. The HAZOP did not document level protection or overflow prevention for the fuel oil storage tank as safeguards. Verify: (a) independent LAH and LAHH instruments on the tank, (b) automatic transfer pump trip on LAHH, (c) bund sizing and drainage arrangement, (d) delivery procedure with operator attendance requirements. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-054 | MAJOR | STG Seals | Common-cause failure vulnerability | All pathways | Common-cause failure vulnerability on STG Seals: 85% of barriers (11/13) are owned by I&C Eng. A systematic failure in that discipline's domain (DCS failure, instrument air loss, staffing gap) would simultaneously degrade the majority of barriers. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Assess common-cause failure modes for I&C Eng-owned barriers on STG Seals. Consider diversifying barrier ownership by adding operational or procedural layers. | Facility Owner | 90 days
F-055 | MAJOR | STG Seals | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on STG Seals: all 6 prevention barriers on 'Initiating event' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Initiating event' pathway on STG Seals. | Facility Owner | 90 days
F-056 | MAJOR | STG Seals | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on STG Seals: all 2 prevention barriers on 'Equipment failure' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Equipment failure' pathway on STG Seals. | Facility Owner | 90 days
F-057 | MAJOR | STG Steam | Single barrier / over-reliance | All pathways | Valve stem leak on extraction or admission valves within the steam turbine casing allows HP/IP/LP steam to escape at the valve bonnet or packing gland. These valves operate at high temperature and pressure with frequent cycling, making packing wear a primary failure mechanism. Standard prevention includes: leak-off connections with monitoring (routed to condenser or drain), packing condition monitoring during operation (visual/thermographic), planned replacement of valve packing during major outages, and live-loading of gland packing. The HAZOP did not document valve-stem-specific safeguards. Verify: (a) leak-off connection arrangement, (b) packing type and replacement schedule, (c) thermographic survey scope includes extraction/admission valve bonnets. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 90 days
F-058 | MAJOR | STG Steam | Common-cause failure vulnerability | All pathways | Common-cause failure vulnerability on STG Steam: 82% of barriers (14/17) are owned by I&C Eng. A systematic failure in that discipline's domain (DCS failure, instrument air loss, staffing gap) would simultaneously degrade the majority of barriers. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Assess common-cause failure modes for I&C Eng-owned barriers on STG Steam. Consider diversifying barrier ownership by adding operational or procedural layers. | Facility Owner | 90 days
F-059 | MAJOR | STG Steam | Defence-in-depth inadequacy | All pathways | Defence-in-depth inadequacy on STG Steam: all 6 prevention barriers on 'Gland steam system failure causing external leak' are 'Hardware - Active'. Per CCPS / EI, defence-in-depth requires barriers from at least 2 of 3 categories (Technical / Operational / Organizational) to protect against common-mode failure. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Identify at least one barrier of a different type (procedural, human, or organizational) for the 'Gland steam system failure causing external leak' pathway on STG Steam. | Facility Owner | 90 days
F-060 | MINOR | Auxiliary Steam | Barrier independence concern | All pathways | Barrier independence concern on Auxiliary Steam: 2 barriers on threat THR-AX-001 share instrument prefix 'VALVE-10', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'VALVE-10' on Auxiliary Steam. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-061 | MINOR | Fuel Gas | Improvement opportunity | PB-FG-036 | Field positioner safeguard PB-FG-036 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-062 | MINOR | Fuel Gas | Improvement opportunity | PB-FG-031 | Field positioner safeguard PB-FG-031 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-063 | MINOR | Fuel Gas | Barrier independence concern | All pathways | Barrier independence concern on Fuel Gas: 2 barriers on threat THR-FG-003 share instrument prefix 'TAL-11EK', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'TAL-11EK' on Fuel Gas. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-064 | MINOR | Fuel Gas | Barrier independence concern | All pathways | Barrier independence concern on Fuel Gas: 5 barriers on threat THR-FG-004 share instrument prefix 'VALVE-11', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'VALVE-11' on Fuel Gas. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-065 | MINOR | Feedwater | Barrier independence concern | All pathways | Barrier independence concern on Feedwater: 2 barriers on threat THR-FW-001 share instrument prefix 'VALVE-11', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'VALVE-11' on Feedwater. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-066 | MINOR | Feedwater | Barrier independence concern | All pathways | Barrier independence concern on Feedwater: 2 barriers on threat THR-FW-001 share instrument prefix 'MOV-11LA', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'MOV-11LA' on Feedwater. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-067 | MINOR | Generator H2 | Barrier independence concern | All pathways | Barrier independence concern on Generator H2: 2 barriers on threat THR-GH-003 share instrument prefix 'PSV-10MK', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'PSV-10MK' on Generator H2. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-068 | MINOR | HRSG IP | Improvement opportunity | PB-HI-014 | Field positioner safeguard PB-HI-014 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-069 | MINOR | HRSG LP | Improvement opportunity | PB-HL-016 | Field positioner safeguard PB-HL-016 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-070 | MINOR | HRSG LP | Improvement opportunity | PB-HL-014 | Field positioner safeguard PB-HL-014 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-071 | MINOR | HRSG LP | Barrier independence concern | All pathways | Barrier independence concern on HRSG LP: 2 barriers on threat THR-HL-001 share instrument prefix 'VALVE-11', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'VALVE-11' on HRSG LP. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-072 | MINOR | HRSG HP | Improvement opportunity | PB-HR-016 | Field positioner safeguard PB-HR-016 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-073 | MINOR | HRSG HP | Improvement opportunity | PB-HR-009 | Field positioner safeguard PB-HR-009 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-074 | MINOR | HRSG HP | Improvement opportunity | PB-HR-007 | Field positioner safeguard PB-HR-007 used as a barrier but SIL rating is not confirmed. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Conduct dedicated barrier review workshop to identify, validate, and document barriers. | Facility Owner | 180 days
F-075 | MINOR | HRSG HP | Barrier independence concern | All pathways | Barrier independence concern on HRSG HP: 3 barriers on threat THR-HR-004 share instrument prefix 'VALVE-11', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'VALVE-11' on HRSG HP. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-076 | MINOR | HRSG HP | Barrier independence concern | All pathways | Barrier independence concern on HRSG HP: 2 barriers on threat THR-HR-004 share instrument prefix 'PDAH-11L', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'PDAH-11L' on HRSG HP. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-077 | MINOR | LP Steam | Barrier independence concern | All pathways | Barrier independence concern on LP Steam: 2 barriers on threat THR-LP-001 share instrument prefix 'MOV-11LB', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'MOV-11LB' on LP Steam. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-078 | MINOR | Ammonia/SCR | Barrier independence concern | All pathways | Barrier independence concern on Ammonia/SCR: 3 barriers on threat THR-NH-001 share instrument prefix 'VALVE-10', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'VALVE-10' on Ammonia/SCR. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days
F-079 | MINOR | STG Steam | Barrier independence concern | All pathways | Barrier independence concern on STG Steam: 5 barriers on threat THR-SS-002 share instrument prefix 'MV10MAL8', suggesting they may share a common sensor, transmitter, or logic solver. Per CCPS / EI, barriers on the same pathway must be independent. | Each pathway shall have at least two independent barriers of differing type per CCPS/EI guidance. | Verify instrument independence for barriers with prefix 'MV10MAL8' on STG Steam. Confirm separate sensors, logic solvers, and final elements. | Facility Owner | 180 days

## SCE Register
SCE ID | Type | System | Barrier ID | Barrier Title | Side | Associated MAH | Consequence Cat. | Functionality | Availability | Reliability | Survivability | Test Interval | Owner
SCE-001 | SCE | ACC | PB-AC-019 | ACC is designed for worst case scenario including opening of LP/IP bypass. | Prevention | MAH-CCGT-AC-001 | D | ACC is designed for worst case scenario including opening of LP/IP bypass.: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-002 | SCE | ACC | PB-AC-018 | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2) | Prevention | MAH-CCGT-AC-001 | D | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-003 | SCE | ACC | PB-AC-017 | MOV-10MAJ45-AA075: Motor operated isolation valve | Prevention | MAH-CCGT-AC-001 | D | MOV-10MAJ45-AA075: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-004 | SCE | ACC | PB-AC-016 | MOV-10LBG45-AA080: Motor operated isolation valve | Prevention | MAH-CCGT-AC-001 | D | MOV-10LBG45-AA080: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-005 | SCE | ACC | PB-AC-015 | PAL-10LBG45-CP001: Pressure alarm low (alert the operator) | Prevention | MAH-CCGT-AC-001 | D | PAL-10LBG45-CP001: Pressure alarm low (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-006 | SCE | ACC | PB-AC-014 | TAH-10MAJ42-CT122: Temperature alarm high (alert the operator) | Prevention | MAH-CCGT-AC-001 | D | TAH-10MAJ42-CT122: Temperature alarm high (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-007 | SCE | ACC | MB-AC-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-AC-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-008 | SCE | ACC | MB-AC-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-AC-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-001 | SCA | ACC | MB-AC-004 | Emergency operating procedures | Mitigation | MAH-CCGT-AC-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-002 | SCA | ACC | MB-AC-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-AC-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-009 | SCE | Auxiliary Steam | MB-AX-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-AX-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-010 | SCE | Auxiliary Steam | MB-AX-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-AX-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-003 | SCA | Auxiliary Steam | MB-AX-004 | Emergency operating procedures | Mitigation | MAH-CCGT-AX-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-004 | SCA | Auxiliary Steam | MB-AX-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-AX-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-011 | SCE | HRSG Bypass | PB-BY-003 | UPS power backup is available for 24 hours for control system. | Prevention | MAH-CCGT-BY-001 | D | UPS power backup is available for 24 hours for control system.: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-012 | SCE | HRSG Bypass | PB-BY-002 | PDAL XYMBR10-CP151/152 | Prevention | MAH-CCGT-BY-001 | D | PDAL XYMBR10-CP151/152: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-013 | SCE | HRSG Bypass | PB-BY-001 | Operator-controlled flue gas supervision | Prevention | MAH-CCGT-BY-001 | D | Operator-controlled flue gas supervision: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-014 | SCE | HRSG Bypass | MB-BY-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-BY-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-015 | SCE | HRSG Bypass | MB-BY-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-BY-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-005 | SCA | HRSG Bypass | MB-BY-004 | Emergency operating procedures | Mitigation | MAH-CCGT-BY-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-006 | SCA | HRSG Bypass | MB-BY-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-BY-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-016 | SCE | HRSG Bypass | MB-BY-005 | Insulation and lagging for personnel protection | Mitigation | MAH-CCGT-BY-001 | D | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-017 | SCE | HRSG Duct Burner | PB-DB-003 | PRV-11HHG01-AA003: Pressure relief valve | Prevention | MAH-CCGT-DB-001 | E | PRV-11HHG01-AA003: Pressure relief valve: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 12 months bench test / 60 months overhaul | MI Eng
SCE-018 | SCE | HRSG Duct Burner | PB-DB-005 | NRV | Prevention | MAH-CCGT-DB-001 | E | NRV: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-019 | SCE | HRSG Duct Burner | PB-DB-004 | FCV-11HHG01-AA101: Flow control valve (control loop regulate downstream flow) | Prevention | MAH-CCGT-DB-001 | E | FCV-11HHG01-AA101: Flow control valve (control loop regulate downstream flow): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-020 | SCE | HRSG Duct Burner | PB-DB-001 | Instrument interlock: instrument interlock and START standby cooling air fan. | Prevention | MAH-CCGT-DB-001 | E | Instrument interlock: instrument interlock and START standby cooling air fan.: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-021 | SCE | HRSG Duct Burner | PB-DB-002 | Instrument interlock: instrument interlock and START standby cooling air fan. | Prevention | MAH-CCGT-DB-001 | E | Instrument interlock: instrument interlock and START standby cooling air fan.: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-022 | SCE | HRSG Duct Burner | MB-DB-001 | Fire and gas detection system | Mitigation | MAH-CCGT-DB-001 | E | Fire and gas detection system: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-023 | SCE | HRSG Duct Burner | MB-DB-002 | F&G interlock to ESDV | Mitigation | MAH-CCGT-DB-001 | E | F&G interlock to ESDV: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-024 | SCE | HRSG Duct Burner | MB-DB-007 | Site emergency response plan | Mitigation | MAH-CCGT-DB-001 | E | Site emergency response plan: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-025 | SCE | HRSG Duct Burner | MB-DB-006 | Hazardous area classification (IEC 60079) | Mitigation | MAH-CCGT-DB-001 | E | Hazardous area classification (IEC 60079): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCE-026 | SCE | HRSG Duct Burner | MB-DB-003 | Firewater deluge / water spray system | Mitigation | MAH-CCGT-DB-001 | E | Firewater deluge / water spray system: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-027 | SCE | HRSG Duct Burner | MB-DB-005 | Fireproofing on structural steel (UL 1709) | Mitigation | MAH-CCGT-DB-001 | E | Fireproofing on structural steel (UL 1709): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCE-028 | SCE | HRSG Duct Burner | MB-DB-004 | Blast rated control room (API 752) | Mitigation | MAH-CCGT-DB-001 | E | Blast rated control room (API 752): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCA-007 | SCA | Fuel Gas | PB-FG-023 | Stack monitoring | Prevention | MAH-CCGT-FG-001 | E | Stack monitoring: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-029 | SCE | Fuel Gas | PB-FG-042 | PAL-00QFB01-CP101A/B: Pressure alarm low (1oo2) | Prevention | MAH-CCGT-FG-001 | E | PAL-00QFB01-CP101A/B: Pressure alarm low (1oo2): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-030 | SCE | Fuel Gas | PB-FG-040 | LSL-00EKC10-CL202: Level switch low (alert the operator) | Prevention | MAH-CCGT-FG-001 | E | LSL-00EKC10-CL202: Level switch low (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-031 | SCE | Fuel Gas | PB-FG-039 | BT00EKC10-BT001: alert the operator | Prevention | MAH-CCGT-FG-001 | E | BT00EKC10-BT001: alert the operator: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-032 | SCE | Fuel Gas | PB-FG-028 | PAL-00EKC50-CP101: Pressure alarm low (00EKC60-CP101 / 00EKC70-CP101 alert the | Prevention | MAH-CCGT-FG-001 | E | PAL-00EKC50-CP101: Pressure alarm low (00EKC60-CP101 / 00EKC70-CP101 alert the: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-033 | SCE | Fuel Gas | PB-FG-024 | LSH-11EKC30-CL202: Level switch high (A/B (1oo) | Prevention | MAH-CCGT-FG-001 | E | LSH-11EKC30-CL202: Level switch high (A/B (1oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-034 | SCE | Fuel Gas | PB-FG-029 | Condensate transfer pump trip/run monitoring | Prevention | MAH-CCGT-FG-001 | E | Condensate transfer pump trip/run monitoring: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-035 | SCE | Fuel Gas | PB-FG-037 | TAH-11EKC30-CT001: Temperature alarm high (A/B (1oo) | Prevention | MAH-CCGT-FG-001 | E | TAH-11EKC30-CT001: Temperature alarm high (A/B (1oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-036 | SCE | Fuel Gas | PB-FG-033 | TAL-11EKC30-CT001: Temperature alarm low (A/B (1oo) | Prevention | MAH-CCGT-FG-001 | E | TAL-11EKC30-CT001: Temperature alarm low (A/B (1oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-037 | SCE | Fuel Gas | PB-FG-032 | TAL-11EKC10-CT002: Temperature alarm low (A/B (1oo) | Prevention | MAH-CCGT-FG-001 | E | TAL-11EKC10-CT002: Temperature alarm low (A/B (1oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-038 | SCE | Fuel Gas | PB-FG-041 | VALVE-00EKC10-AA402: Valve position confirmation ON/OFF | Prevention | MAH-CCGT-FG-001 | E | VALVE-00EKC10-AA402: Valve position confirmation ON/OFF: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-039 | SCE | Fuel Gas | PB-FG-038 | VALVE-11EKT20-AA109: Valve position confirmation pneumatic ON/OFF | Prevention | MAH-CCGT-FG-001 | E | VALVE-11EKT20-AA109: Valve position confirmation pneumatic ON/OFF: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-040 | SCE | Fuel Gas | PB-FG-036 | VALVE-11EKT20-AA113: Pneumatic control valve positioner | Prevention | MAH-CCGT-FG-001 | E | VALVE-11EKT20-AA113: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-041 | SCE | Fuel Gas | PB-FG-035 | VALVE-11EKT20-AA106: Valve position confirmation pneumatic ON/OFF | Prevention | MAH-CCGT-FG-001 | E | VALVE-11EKT20-AA106: Valve position confirmation pneumatic ON/OFF: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-042 | SCE | Fuel Gas | PB-FG-034 | VALVE-11EKT20-AA101: Valve position confirmation pneumatic ON/OFF | Prevention | MAH-CCGT-FG-001 | E | VALVE-11EKT20-AA101: Valve position confirmation pneumatic ON/OFF: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-043 | SCE | Fuel Gas | PB-FG-031 | VALVE-11EKT10-AA111: Pneumatic control valve positioner | Prevention | MAH-CCGT-FG-001 | E | VALVE-11EKT10-AA111: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-044 | SCE | Fuel Gas | MB-FG-001 | AAH-00EKC10-AI002: Gas detection alarm (20% LEL) | Mitigation | MAH-CCGT-FG-001 | E | AAH-00EKC10-AI002: Gas detection alarm (20% LEL): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-045 | SCE | Fuel Gas | MB-FG-002 | Fire and gas detection system | Mitigation | MAH-CCGT-FG-001 | E | Fire and gas detection system: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-046 | SCE | Fuel Gas | MB-FG-003 | F&G interlock to ESDV | Mitigation | MAH-CCGT-FG-001 | E | F&G interlock to ESDV: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-047 | SCE | Fuel Gas | MB-FG-004 | Firewater deluge / water spray system | Mitigation | MAH-CCGT-FG-001 | E | Firewater deluge / water spray system: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-048 | SCE | Fuel Gas | MB-FG-008 | Site emergency response plan | Mitigation | MAH-CCGT-FG-001 | E | Site emergency response plan: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-049 | SCE | Fuel Gas | MB-FG-006 | Fireproofing on structural steel (UL 1709) | Mitigation | MAH-CCGT-FG-001 | E | Fireproofing on structural steel (UL 1709): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCE-050 | SCE | Fuel Gas | MB-FG-005 | Blast rated control room (API 752) | Mitigation | MAH-CCGT-FG-001 | E | Blast rated control room (API 752): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCE-051 | SCE | Fuel Oil | MB-FO-001 | Gas detection system (from F&G) | Mitigation | MAH-CCGT-FO-001 | E | Gas detection system (from F&G): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-052 | SCE | Fuel Oil | MB-FO-006 | Spill response kit | Mitigation | MAH-CCGT-FO-001 | E | Spill response kit: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-053 | SCE | Fuel Oil | MB-FO-007 | Site emergency response plan | Mitigation | MAH-CCGT-FO-001 | E | Site emergency response plan: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-054 | SCE | Fuel Oil | MB-FO-004 | Bund containment around tank (API 650) | Mitigation | MAH-CCGT-FO-001 | E | Bund containment around tank (API 650): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCE-055 | SCE | Fuel Oil | MB-FO-002 | Flame / fire detection (from F&G) | Mitigation | MAH-CCGT-FO-001 | E | Flame / fire detection (from F&G): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-056 | SCE | Fuel Oil | MB-FO-003 | Fire detection in oil area | Mitigation | MAH-CCGT-FO-001 | E | Fire detection in oil area: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-057 | SCE | Fuel Oil | MB-FO-005 | Fire suppression (CO2 / water spray) | Mitigation | MAH-CCGT-FO-001 | E | Fire suppression (CO2 / water spray): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-058 | SCE | Feedwater | MB-FW-003 | Emergency isolation valve | Mitigation | MAH-CCGT-FW-001 | E | Emergency isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-059 | SCE | Feedwater | MB-FW-004 | Insulation and lagging for personnel protection | Mitigation | MAH-CCGT-FW-001 | E | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-060 | SCE | Feedwater | MB-FW-001 | Leak detection and area drainage | Mitigation | MAH-CCGT-FW-001 | E | Leak detection and area drainage: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCA-008 | SCA | Feedwater | MB-FW-002 | Access restriction to BFP area | Mitigation | MAH-CCGT-FW-001 | E | Access restriction to BFP area: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-061 | SCE | Generator H2 | PB-GH-003 | PSL10MKG21-CP101: alert the operator | Prevention | MAH-CCGT-GH-001 | E | PSL10MKG21-CP101: alert the operator: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-062 | SCE | Generator H2 | PB-GH-002 | PSH10MKG21-CP102: alert the operator | Prevention | MAH-CCGT-GH-001 | E | PSH10MKG21-CP102: alert the operator: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-063 | SCE | Generator H2 | PB-GH-001 | PAL-00PGB07-CP101A/B: Pressure alarm low (1oo2) | Prevention | MAH-CCGT-GH-001 | E | PAL-00PGB07-CP101A/B: Pressure alarm low (1oo2): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-064 | SCE | Generator H2 | PB-GH-005 | PSV-10MKG42-AA191: release excess pressure above [TBC] BARG to safe location | Prevention | MAH-CCGT-GH-001 | E | PSV-10MKG42-AA191: release excess pressure above [TBC] BARG to safe location: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 12 months bench test / 60 months overhaul | MI Eng
SCE-065 | SCE | Generator H2 | PB-GH-004 | PSV-10MKG10-AA191: 10MKG01-AA191 release excess pressure above 210 BARG to | Prevention | MAH-CCGT-GH-001 | E | PSV-10MKG10-AA191: 10MKG01-AA191 release excess pressure above 210 BARG to: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 12 months bench test / 60 months overhaul | MI Eng
SCE-066 | SCE | Generator H2 | MB-GH-001 | H2-specific catalytic detector | Mitigation | MAH-CCGT-GH-001 | E | H2-specific catalytic detector: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-067 | SCE | Generator H2 | MB-GH-002 | Ventilation system with gas interlock | Mitigation | MAH-CCGT-GH-001 | E | Ventilation system with gas interlock: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-068 | SCE | Generator H2 | MB-GH-005 | Hazardous area classification (IEC 60079) | Mitigation | MAH-CCGT-GH-001 | E | Hazardous area classification (IEC 60079): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCE-069 | SCE | Generator H2 | MB-GH-003 | Explosion relief panels | Mitigation | MAH-CCGT-GH-001 | E | Explosion relief panels: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-070 | SCE | Generator H2 | MB-GH-004 | Blast-rated generator building (API 752) | Mitigation | MAH-CCGT-GH-001 | E | Blast-rated generator building (API 752): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCE-071 | SCE | HRSG IP | PB-HI-012 | NRV-11LBA20-AA201: Non-return valve | Prevention | MAH-CCGT-HI-001 | E | NRV-11LBA20-AA201: Non-return valve: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCA-009 | SCA | HRSG IP | PB-HI-015 | Online sampling of water / steam | Prevention | MAH-CCGT-HI-001 | E | Online sampling of water / steam: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-010 | SCA | HRSG IP | PB-HI-013 | Annual preventive maintenance schedule | Prevention | MAH-CCGT-HI-001 | E | Annual preventive maintenance schedule: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-072 | SCE | HRSG IP | PB-HI-014 | VALVE-11HAC30-AA101: Pneumatic control valve positioner | Prevention | MAH-CCGT-HI-001 | E | VALVE-11HAC30-AA101: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-073 | SCE | HRSG IP | PB-HI-011 | LAH-11HAD20-CL121: Level alarm high (A/B/C (2oo) | Prevention | MAH-CCGT-HI-001 | E | LAH-11HAD20-CL121: Level alarm high (A/B/C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-074 | SCE | HRSG IP | PB-HI-010 | MOV-11LBB10-AA102: Motor operated isolation valve | Prevention | MAH-CCGT-HI-001 | E | MOV-11LBB10-AA102: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-075 | SCE | HRSG IP | MB-HI-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-HI-001 | E | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-076 | SCE | HRSG IP | MB-HI-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-HI-001 | E | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-011 | SCA | HRSG IP | MB-HI-004 | Emergency operating procedures | Mitigation | MAH-CCGT-HI-001 | E | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-012 | SCA | HRSG IP | MB-HI-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-HI-001 | E | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-077 | SCE | HRSG IP | MB-HI-005 | Insulation and lagging for personnel protection | Mitigation | MAH-CCGT-HI-001 | E | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-078 | SCE | HRSG LP | PB-HL-013 | NRV-11LBA10-AA201: Non-return valve | Prevention | MAH-CCGT-HL-001 | E | NRV-11LBA10-AA201: Non-return valve: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCA-013 | SCA | HRSG LP | PB-HL-017 | Online sampling of water / steam | Prevention | MAH-CCGT-HL-001 | E | Online sampling of water / steam: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-014 | SCA | HRSG LP | PB-HL-015 | Annual preventive maintenance schedule | Prevention | MAH-CCGT-HL-001 | E | Annual preventive maintenance schedule: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-079 | SCE | HRSG LP | PB-HL-016 | VALVE-11LAB61-AA102: Pneumatic control valve positioner | Prevention | MAH-CCGT-HL-001 | E | VALVE-11LAB61-AA102: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-080 | SCE | HRSG LP | PB-HL-014 | VALVE-11LAB63-AA101: Pneumatic control valve positioner | Prevention | MAH-CCGT-HL-001 | E | VALVE-11LAB63-AA101: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-081 | SCE | HRSG LP | PB-HL-011 | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo) | Prevention | MAH-CCGT-HL-001 | E | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-082 | SCE | HRSG LP | PB-HL-009 | PSV-11LBA30-AA191: PSV set (PSV-11HAD30-AA191 and 11HAD30-AA192 | Prevention | MAH-CCGT-HL-001 | E | PSV-11LBA30-AA191: PSV set (PSV-11HAD30-AA191 and 11HAD30-AA192: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 12 months bench test / 60 months overhaul | MI Eng
SCE-083 | SCE | HRSG LP | PB-HL-012 | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo) | Prevention | MAH-CCGT-HL-001 | E | PAH-11HAD30-CP121: Pressure alarm high (A/B/C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-084 | SCE | HRSG LP | MB-HL-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-HL-001 | E | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-085 | SCE | HRSG LP | MB-HL-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-HL-001 | E | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-015 | SCA | HRSG LP | MB-HL-004 | Emergency operating procedures | Mitigation | MAH-CCGT-HL-001 | E | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-016 | SCA | HRSG LP | MB-HL-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-HL-001 | E | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCA-017 | SCA | HP Steam | PB-HP-010 | Online sampling of water / steam | Prevention | MAH-CCGT-HP-001 | D | Online sampling of water / steam: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-086 | SCE | HP Steam | PB-HP-009 | High alarm with instrument interlock (auto-trip) | Prevention | MAH-CCGT-HP-001 | D | High alarm with instrument interlock (auto-trip): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-087 | SCE | HP Steam | PB-HP-006 | FOR10LBA01-AA409: Valve position feedback | Prevention | MAH-CCGT-HP-001 | D | FOR10LBA01-AA409: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-088 | SCE | HP Steam | PB-HP-005 | VALVE-11LBA02-AA101: Valve position feedback | Prevention | MAH-CCGT-HP-001 | D | VALVE-11LBA02-AA101: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-089 | SCE | HP Steam | PB-HP-004 | FOR11LBA02-AA001: Valve position feedback | Prevention | MAH-CCGT-HP-001 | D | FOR11LBA02-AA001: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-090 | SCE | HP Steam | PB-HP-003 | PAH-10LBA03-CP121A/B: Pressure alarm high (1oo2) | Prevention | MAH-CCGT-HP-001 | D | PAH-10LBA03-CP121A/B: Pressure alarm high (1oo2): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-091 | SCE | HP Steam | PB-HP-007 | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow. | Prevention | MAH-CCGT-HP-001 | D | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow.: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCE-092 | SCE | HP Steam | PB-HP-008 | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow. | Prevention | MAH-CCGT-HP-001 | D | NRV is provided in discharge HP steam line of each HRSG to prevent reverse flow.: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCE-093 | SCE | HP Steam | PB-HP-002 | MOV: Motor operated isolation valve | Prevention | MAH-CCGT-HP-001 | D | MOV: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-094 | SCE | HP Steam | MB-HP-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-HP-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-095 | SCE | HP Steam | MB-HP-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-HP-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-018 | SCA | HP Steam | MB-HP-004 | Emergency operating procedures | Mitigation | MAH-CCGT-HP-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-019 | SCA | HP Steam | MB-HP-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-HP-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-096 | SCE | HP Steam | MB-HP-005 | Insulation and lagging for personnel protection | Mitigation | MAH-CCGT-HP-001 | D | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-097 | SCE | HRSG HP | PB-HR-015 | NRV-11LBA10-AA201: Non-return valve | Prevention | MAH-CCGT-HR-001 | D | NRV-11LBA10-AA201: Non-return valve: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCA-020 | SCA | HRSG HP | PB-HR-018 | Online sampling of water / steam | Prevention | MAH-CCGT-HR-001 | D | Online sampling of water / steam: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-021 | SCA | HRSG HP | PB-HR-017 | Annual preventive maintenance schedule | Prevention | MAH-CCGT-HR-001 | D | Annual preventive maintenance schedule: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-098 | SCE | HRSG HP | PB-HR-014 | LAH-11HAD10-CL121: Level alarm high (A/B/C (2oo) | Prevention | MAH-CCGT-HR-001 | D | LAH-11HAD10-CL121: Level alarm high (A/B/C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-099 | SCE | HRSG HP | PB-HR-012 | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo) | Prevention | MAH-CCGT-HR-001 | D | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-100 | SCE | HRSG HP | PB-HR-011 | MOV-11LBA10-AA102: Motor operated isolation valve | Prevention | MAH-CCGT-HR-001 | D | MOV-11LBA10-AA102: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-101 | SCE | HRSG HP | PB-HR-016 | VALVE-11LAB63-AA101: Pneumatic control valve positioner | Prevention | MAH-CCGT-HR-001 | D | VALVE-11LAB63-AA101: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-102 | SCE | HRSG HP | PB-HR-013 | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo) | Prevention | MAH-CCGT-HR-001 | D | PAH-11HAD10-CP121A/B: Pressure alarm high (C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-103 | SCE | HRSG HP | PB-HR-009 | VALVE-11LAE10-AA102: Pneumatic control valve positioner | Prevention | MAH-CCGT-HR-001 | D | VALVE-11LAE10-AA102: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-104 | SCE | HRSG HP | PB-HR-008 | PDAH-11LAE40-CF181: Differential pressure alarm high (alert the operator) | Prevention | MAH-CCGT-HR-001 | D | PDAH-11LAE40-CF181: Differential pressure alarm high (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-105 | SCE | HRSG HP | PB-HR-007 | VALVE-11LAE10-AA104: Pneumatic control valve positioner | Prevention | MAH-CCGT-HR-001 | D | VALVE-11LAE10-AA104: Pneumatic control valve positioner: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-106 | SCE | HRSG HP | PB-HR-005 | PDAH-11LAE10-CP181: Differential pressure alarm high (alert the operator) | Prevention | MAH-CCGT-HR-001 | D | PDAH-11LAE10-CP181: Differential pressure alarm high (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-107 | SCE | HRSG HP | MB-HR-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-HR-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-108 | SCE | HRSG HP | MB-HR-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-HR-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-022 | SCA | HRSG HP | MB-HR-004 | Emergency operating procedures | Mitigation | MAH-CCGT-HR-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-023 | SCA | HRSG HP | MB-HR-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-HR-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-109 | SCE | HRSG HP | MB-HR-005 | Insulation and lagging for personnel protection | Mitigation | MAH-CCGT-HR-001 | D | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-110 | SCE | LP Steam | PB-LP-006 | NRV is provided in discharge LP steam line of each HRSG to prevent reverse flow. | Prevention | MAH-CCGT-LP-001 | D | NRV is provided in discharge LP steam line of each HRSG to prevent reverse flow.: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCA-024 | SCA | LP Steam | PB-LP-008 | Online sampling of water / steam | Prevention | MAH-CCGT-LP-001 | D | Online sampling of water / steam: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-111 | SCE | LP Steam | PB-LP-007 | LABLE11LBA30-CT121: Temperature elements are avai A/B (1oo2)to generate high | Prevention | MAH-CCGT-LP-001 | D | LABLE11LBA30-CT121: Temperature elements are avai A/B (1oo2)to generate high: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-112 | SCE | LP Steam | PB-LP-005 | FOR10LBD02-AA405: Valve position feedback | Prevention | MAH-CCGT-LP-001 | D | FOR10LBD02-AA405: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-113 | SCE | LP Steam | PB-LP-004 | MOV-11LBD01-AA402: Motor operated isolation valve | Prevention | MAH-CCGT-LP-001 | D | MOV-11LBD01-AA402: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-114 | SCE | LP Steam | PB-LP-001 | MOV-11LBD01-AA001: Motor operated isolation valve | Prevention | MAH-CCGT-LP-001 | D | MOV-11LBD01-AA001: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-115 | SCE | LP Steam | MB-LP-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-LP-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-116 | SCE | LP Steam | MB-LP-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-LP-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-025 | SCA | LP Steam | MB-LP-004 | Emergency operating procedures | Mitigation | MAH-CCGT-LP-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-026 | SCA | LP Steam | MB-LP-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-LP-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCA-027 | SCA | Ammonia/SCR | PB-NH-001 | Operator continuous attendance (manual control) | Prevention | MAH-CCGT-NH-001 | A | Operator continuous attendance (manual control): operator detects and responds within alarm response time | Continuous attendance during operation | Minimum two qualified operators per shift | Operator accessible during design-basis event | 6 months drill / annual competency | Operations
SCE-117 | SCE | Ammonia/SCR | PB-NH-004 | VALVE-10GHD41-AA102: Valve position feedback | Prevention | MAH-CCGT-NH-001 | A | VALVE-10GHD41-AA102: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-118 | SCE | Ammonia/SCR | PB-NH-003 | VALVE-10GHD41-AA104: Valve position feedback | Prevention | MAH-CCGT-NH-001 | A | VALVE-10GHD41-AA104: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-119 | SCE | Ammonia/SCR | PB-NH-002 | VALVE-10GHD41-AA103: Valve position feedback | Prevention | MAH-CCGT-NH-001 | A | VALVE-10GHD41-AA103: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-120 | SCE | Ammonia/SCR | MB-NH-001 | Toxic gas detection (NH3) | Mitigation | MAH-CCGT-NH-001 | A | Toxic gas detection (NH3): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-121 | SCE | Ammonia/SCR | MB-NH-003 | SCBA availability at unloading bay | Mitigation | MAH-CCGT-NH-001 | A | SCBA availability at unloading bay: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-122 | SCE | Ammonia/SCR | MB-NH-004 | Emergency shower and eyewash | Mitigation | MAH-CCGT-NH-001 | A | Emergency shower and eyewash: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-123 | SCE | Ammonia/SCR | MB-NH-006 | Site emergency response plan | Mitigation | MAH-CCGT-NH-001 | A | Site emergency response plan: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCA-028 | SCA | Ammonia/SCR | MB-NH-005 | Exclusion zone during transfers | Mitigation | MAH-CCGT-NH-001 | A | Exclusion zone during transfers: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-124 | SCE | Ammonia/SCR | MB-NH-002 | Water curtain / spray system | Mitigation | MAH-CCGT-NH-001 | A | Water curtain / spray system: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCA-029 | SCA | STG Steam | PB-SS-004 | Operator continuous attendance (manual control) | Prevention | MAH-CCGT-SS-001 | D | Operator continuous attendance (manual control): operator detects and responds within alarm response time | Continuous attendance during operation | Minimum two qualified operators per shift | Operator accessible during design-basis event | 6 months drill / annual competency | Operations
SCE-125 | SCE | STG Steam | PB-SS-023 | PCV: Pressure control valve (LCE81-AA001 is available in upstream to regulate | Prevention | MAH-CCGT-SS-001 | D | PCV: Pressure control valve (LCE81-AA001 is available in upstream to regulate: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-126 | SCE | STG Steam | PB-SS-022 | PCV-10LCE81-AA001: Pressure control valve (Field positioner / Discrepancy | Prevention | MAH-CCGT-SS-001 | D | PCV-10LCE81-AA001: Pressure control valve (Field positioner / Discrepancy: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-127 | SCE | STG Steam | PB-SS-021 | PDAH-10LCE81-CP122: Differential pressure alarm high (alert the operator) | Prevention | MAH-CCGT-SS-001 | D | PDAH-10LCE81-CP122: Differential pressure alarm high (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-128 | SCE | STG Steam | PB-SS-020 | TAH-10MAC81-CT053A/B: Temperature alarm high (C (2oo) | Prevention | MAH-CCGT-SS-001 | D | TAH-10MAC81-CT053A/B: Temperature alarm high (C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-129 | SCE | STG Steam | PB-SS-019 | FCV: Flow control valve (Field positioner / Discrepancy position feedback | Prevention | MAH-CCGT-SS-001 | D | FCV: Flow control valve (Field positioner / Discrepancy position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-130 | SCE | STG Steam | PB-SS-028 | MV10MAL95-AA401: Valve position feedback | Prevention | MAH-CCGT-SS-001 | D | MV10MAL95-AA401: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-131 | SCE | STG Steam | PB-SS-027 | MV10MAL87-AA401: Valve position feedback | Prevention | MAH-CCGT-SS-001 | D | MV10MAL87-AA401: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-132 | SCE | STG Steam | PB-SS-026 | MV10MAL82-AA401: Valve position feedback | Prevention | MAH-CCGT-SS-001 | D | MV10MAL82-AA401: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-133 | SCE | STG Steam | PB-SS-025 | MV10MAL83-AA401: Valve position feedback | Prevention | MAH-CCGT-SS-001 | D | MV10MAL83-AA401: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-134 | SCE | STG Steam | PB-SS-024 | MV10MAL81-AA401: Valve position feedback | Prevention | MAH-CCGT-SS-001 | D | MV10MAL81-AA401: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-135 | SCE | STG Steam | PB-SS-018 | MV10MAL86-AA401: Valve position feedback | Prevention | MAH-CCGT-SS-001 | D | MV10MAL86-AA401: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-136 | SCE | STG Steam | MB-SS-001 | Steam leak detection and alarm | Mitigation | MAH-CCGT-SS-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-137 | SCE | STG Steam | MB-SS-003 | Emergency isolation (remote operated) | Mitigation | MAH-CCGT-SS-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-030 | SCA | STG Steam | MB-SS-004 | Emergency operating procedures | Mitigation | MAH-CCGT-SS-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-031 | SCA | STG Steam | MB-SS-002 | Access restriction and exclusion zones | Mitigation | MAH-CCGT-SS-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-138 | SCE | STG Steam | MB-SS-005 | Insulation and lagging for personnel protection | Mitigation | MAH-CCGT-SS-001 | D | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-139 | SCE | CRH Steam | PB-CR-003 | VALVE-10LBC01-AA402: Valve position feedback | Prevention | MAH-001 | D | VALVE-10LBC01-AA402: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-140 | SCE | CRH Steam | PB-CR-002 | MOV-12LBC01-AA410: Motor operated isolation valve | Prevention | MAH-001 | D | MOV-12LBC01-AA410: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-141 | SCE | CRH Steam | PB-CR-001 | MOV-11LBC01-AA001: Motor operated isolation valve | Prevention | MAH-001 | D | MOV-11LBC01-AA001: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-142 | SCE | CRH Steam | PB-AC-018-X-CD | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2) | Prevention | MAH-001 | D | FAL-10LCA04-CF101A/B: Flow alarm low (1oo2): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-143 | SCE | CRH Steam | MB-CR-003 | Insulation and lagging for personnel protection | Mitigation | MAH-001 | D | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-144 | SCE | CRH Steam | MB-CR-001 | Drain routing to safe location | Mitigation | MAH-001 | D | Drain routing to safe location: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCA-032 | SCA | CRH Steam | MB-CR-002 | Access restriction | Mitigation | MAH-001 | D | Access restriction: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCA-033 | SCA | HRH Steam | PB-HH-006 | Positive isolation (energy isolation for maintenance) | Prevention | MAH-001 | D | Positive isolation (energy isolation for maintenance): management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCA-034 | SCA | HRH Steam | PB-HH-008 | Online sampling of water / steam | Prevention | MAH-001 | D | Online sampling of water / steam: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-145 | SCE | HRH Steam | PB-HH-007 | LABLE11LBB10-CT123: Temperature elements are avai A/B/C to generate high | Prevention | MAH-001 | D | LABLE11LBB10-CT123: Temperature elements are avai A/B/C to generate high: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-146 | SCE | HRH Steam | PB-HH-003 | PAH-10LBB01-CP121A/B: Pressure alarm high (1oo2)and PAL-10LBB01-CP122 is | Prevention | MAH-001 | D | PAH-10LBB01-CP121A/B: Pressure alarm high (1oo2)and PAL-10LBB01-CP122 is: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-147 | SCE | HRH Steam | PB-HH-001 | FAL-11LBB10-CF121A/B: Flow alarm low (1oo2) | Prevention | MAH-001 | D | FAL-11LBB10-CF121A/B: Flow alarm low (1oo2): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-148 | SCE | HRH Steam | PB-HH-005 | FOR10LBB01-AA412: Valve position feedback | Prevention | MAH-001 | D | FOR10LBB01-AA412: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-149 | SCE | HRH Steam | PB-HH-004 | VALVE-11LBB01-AA101: Valve position feedback | Prevention | MAH-001 | D | VALVE-11LBB01-AA101: Valve position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-150 | SCE | HRH Steam | PB-HH-002 | MOV: Motor operated isolation valve | Prevention | MAH-001 | D | MOV: Motor operated isolation valve: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-151 | SCE | HRH Steam | MB-HH-001 | Steam leak detection and alarm | Mitigation | MAH-001 | D | Steam leak detection and alarm: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-152 | SCE | HRH Steam | MB-HH-003 | Emergency isolation (remote operated) | Mitigation | MAH-001 | D | Emergency isolation (remote operated): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-153 | SCE | HRH Steam | MB-HH-005 | Insulation and lagging for personnel protection | Mitigation | MAH-001 | D | Insulation and lagging for personnel protection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCA-035 | SCA | HRH Steam | MB-HH-004 | Emergency operating procedures | Mitigation | MAH-001 | D | Emergency operating procedures: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCA-036 | SCA | HRH Steam | MB-HH-002 | Access restriction and exclusion zones | Mitigation | MAH-001 | D | Access restriction and exclusion zones: management system in place, auditable, and enforced | Continuous (management system) | Annual audit against procedure requirements | N/A (management control) | 12 months management review | HSSE
SCE-154 | SCE | STG Seals | PB-SL-014 | LAH-10MKW01-CL101: Level alarm high (alert the operator) | Prevention | MAH-001 | E | LAH-10MKW01-CL101: Level alarm high (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-155 | SCE | STG Seals | PB-SL-013 | ECTOR10MKW21-BZ001: SODE will overflow to liquid det and alert the operator | Prevention | MAH-001 | E | ECTOR10MKW21-BZ001: SODE will overflow to liquid det and alert the operator: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-156 | SCE | STG Seals | PB-SL-012 | PSL10MKG21-CP101: alert the operator | Prevention | MAH-001 | E | PSL10MKG21-CP101: alert the operator: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-157 | SCE | STG Seals | PB-SL-011 | Pump discharge line is designed for pump shut-off head. | Prevention | MAH-001 | E | Pump discharge line is designed for pump shut-off head.: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-158 | SCE | STG Seals | PB-SL-010 | FAL-10MKW06-CF001: Flow alarm low (alert the operator) | Prevention | MAH-001 | E | FAL-10MKW06-CF001: Flow alarm low (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-159 | SCE | STG Seals | PB-SL-009 | PDAH-10MKW10-CP001: Differential pressure alarm high (A/B (1oo) | Prevention | MAH-001 | E | PDAH-10MKW10-CP001: Differential pressure alarm high (A/B (1oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-160 | SCE | STG Seals | PB-SL-004 | Auto start of standby Gland condenser blower on tripping of duty blower. | Prevention | MAH-001 | E | Auto start of standby Gland condenser blower on tripping of duty blower.: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-161 | SCE | STG Seals | PB-SL-002 | PCV: Pressure control valve (Field positioner / Discrepancy position feedback | Prevention | MAH-001 | E | PCV: Pressure control valve (Field positioner / Discrepancy position feedback: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-162 | SCE | STG Seals | MB-SL-001 | H2-specific catalytic detector | Mitigation | MAH-001 | E | H2-specific catalytic detector: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-163 | SCE | STG Seals | MB-SL-002 | Ventilation system with gas interlock | Mitigation | MAH-001 | E | Ventilation system with gas interlock: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-164 | SCE | STG Seals | MB-SL-003 | Explosion relief panels | Mitigation | MAH-001 | E | Explosion relief panels: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-165 | SCE | STG Seals | MB-SL-004 | Blast-rated generator building (API 752) | Mitigation | MAH-001 | E | Blast-rated generator building (API 752): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCE-166 | SCE | STG Seals | MB-SL-005 | Hazardous area classification (IEC 60079) | Mitigation | MAH-001 | E | Hazardous area classification (IEC 60079): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | MI Eng
SCA-037 | SCA | STG Lube Oil | PB-LO-005 | Turn around PM schedule is available | Prevention | MAH-001 | D | Turn around PM schedule is available: executed per schedule with documented evidence | Per schedule (not demand-based) | Competency-verified personnel; procedure reviewed annually | N/A (administrative control) | 12 months procedure review | Operations
SCE-167 | SCE | STG Lube Oil | PB-LO-004 | TAH-10MAV95-CT122: Temperature alarm high (A/B (1oo) | Prevention | MAH-001 | D | TAH-10MAV95-CT122: Temperature alarm high (A/B (1oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-168 | SCE | STG Lube Oil | PB-LO-003 | PAH-10MAV95-CP125: Pressure alarm high (A/B/C (2oo) | Prevention | MAH-001 | D | PAH-10MAV95-CP125: Pressure alarm high (A/B/C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-169 | SCE | STG Lube Oil | PB-LO-002 | PDAH-10MAV93-CP181: Differential pressure alarm high (alert the operator) | Prevention | MAH-001 | D | PDAH-10MAV93-CP181: Differential pressure alarm high (alert the operator): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-170 | SCE | STG Lube Oil | PB-LO-001 | PAL-10MAV95-CP125: Pressure alarm low (A/B/C (2oo) | Prevention | MAH-001 | D | PAL-10MAV95-CP125: Pressure alarm low (A/B/C (2oo): actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-171 | SCE | STG Lube Oil | MB-LO-001 | Oil mist detection | Mitigation | MAH-001 | D | Oil mist detection: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-172 | SCE | STG Lube Oil | MB-LO-002 | CO2 / clean agent fire suppression | Mitigation | MAH-001 | D | CO2 / clean agent fire suppression: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | I&C Eng
SCE-173 | SCE | STG Lube Oil | MB-LO-004 | Flame detection near hot surfaces | Mitigation | MAH-001 | D | Flame detection near hot surfaces: actuates within design response time on demand | >=99% availability (planned maintenance windows excluded) | PFD per IEC 61511 - to be confirmed at site | Maintain function under design-basis fire/blast conditions | 12 months proof test | HSSE
SCE-174 | SCE | STG Lube Oil | MB-LO-003 | Drip trays and bund containment | Mitigation | MAH-001 | D | Drip trays and bund containment: maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng
SCE-175 | SCE | STG Lube Oil | MB-LO-005 | Fireproofing on structural steel (UL 1709) | Mitigation | MAH-001 | D | Fireproofing on structural steel (UL 1709): maintains integrity under design pressure and temperature | >=99.9% availability (passive device) | Inspection per API 510/ASME - no demand-based failure mechanism | Withstand design-basis operating conditions | 24 months inspection | Project Eng

## Summary
Copy_of_Qasim_HAZOP_report_Excel.xlsx -- Bowtie Risk Assessment Training Data
Evidence confidence cap: 65/100 (desk review) ¦ Structural confidence: 85%
Facility
Facility name | Copy_of_Qasim_HAZOP_report_Excel.xlsx
Technology | CCGT
Source file | /data/output/5faf482a-0a49-4aff-9571-ef6a5e03c66c/input.xlsx
Generated | 2026-04-27T03:18:07+00:00
Dataset Metrics
Bowtie systems | 19
Total elements | 368
Threats | 47
Consequences | 50
Prevention barriers | 134
Mitigation barriers | 99
Total barriers | 233
Gap findings (total) | 83
CRITICAL | 25
MAJOR | 38
MINOR | 20
SCE | 175
SCA | 37
Barrier Provenance Breakdown
Tier | Count | Definition
From HAZOP | 135 | Row-level verified with instrument tags
From HAZOP (limited) | 0 | Traceable but sparse HAZOP support
Aggregated from HAZOP | 0 | Synthesised from multiple HAZOP rows
Derived from HAZOP | 0 | Logically inferred from HAZOP data
Engineering standard | 15 | Based on industry code / standard
Domain knowledge | 3 | Expert knowledge (HAZOP gap)
Suggested | 0 | Gap-fill requiring site validation
System Summary
System | Threats | Consequences | Prevention | Mitigation | Gaps
ACC | 2 | 2 | 6 | 5 | 2
Auxiliary Steam | 2 | 2 | 6 | 5 | 2
HRSG Bypass | 2 | 3 | 3 | 5 | 2
HRSG Duct Burner | 2 | 3 | 5 | 7 | 2
Fuel Gas | 4 | 2 | 16 | 7 | 3
Fuel Oil | 3 | 3 | 0 | 7 | 3
Feedwater | 2 | 2 | 9 | 4 | 1
Generator H2 | 3 | 1 | 5 | 5 | 2
HRSG IP | 2 | 2 | 6 | 5 | 3
HRSG LP | 2 | 2 | 8 | 5 | 3
HP Steam | 4 | 3 | 9 | 5 | 3
HRSG HP | 4 | 2 | 12 | 5 | 6
LP Steam | 2 | 2 | 8 | 5 | 1
Ammonia/SCR | 3 | 1 | 4 | 6 | 3
STG Steam | 3 | 3 | 12 | 5 | 2
CRH Steam | 1 | 3 | 4 | 3 | 1
HRH Steam | 2 | 5 | 8 | 5 | 1
STG Seals | 2 | 8 | 8 | 5 | 1
STG Lube Oil | 2 | 1 | 5 | 5 | 2
Known Limitations
1. Desk-review evidence cap 65/100 (non-negotiable).
2. PFD and SIL values require site validation; defaults seeded from catalogue.
3. Suggested barriers (blue rows) are gap-fill candidates.
4. FARSI performance standards are templates; site refinement required.

## HAZOP Source Map
Bowtie System | HAZOP Node(s) | HAZOP Node Name | Rows | S>=3 Scenarios | Notes
ACC | 56. ACC NODE 1 Steam & Condensate Collection System,57. ACC NODE 2 Vacuum System | 56. ACC NODE 1 Steam & Condensate Collection System | 26 | 22 | Full coverage; 4 row(s) below S>=3 threshold excluded.
Ammonia/SCR | 24. HRSG NODE 08 Ammonia unloading system TYPICAL (for HRSG 11, 12 and 13),25. HRSG NODE 09 Ammonia Consumption system TYPICAL (for HRSG 11, 12 and 13) | 24. HRSG NODE 08 Ammonia unloading system TYPICAL (for HRSG 11, 12 and 13) | 12 | 5 | Full coverage; 7 row(s) below S>=3 threshold excluded.
Auxiliary Steam | 5. Auxiliary steam system | 5. Auxiliary steam system | 28 | 4 | Full coverage; 24 row(s) below S>=3 threshold excluded.
CRH Steam | 2. CRH Steam System | 2. CRH Steam System | 11 | 5 | Full coverage; 6 row(s) below S>=3 threshold excluded.
Feedwater | 8. Feed water system (TYPICAL) | 8. Feed water system (TYPICAL) | 21 | 15 | Full coverage; 6 row(s) below S>=3 threshold excluded.
Fuel Gas | 39. FGS NODE 1 Fuel gas booster compressor,42. FGS NODE 4 Emergency shutdown valve (ESDV) skid, Settlement metering & back up metering skid, Conditioning skid and Pressure reducing skid,43. FGS NODE 5 Dedicated pressure reducing station (PRCS) skid for GT #14 including startup and common heater skid,44. FGS NODE 6 Pressure reducing station (PRCS) skid for HRSG & AUX. Boiler,46. FGS NODE 8 HP performance heater skid for GT # 11, 12 & 13 (TYPICAL),47. FGS NODE 9 Cold vent stack along with collection system | 39. FGS NODE 1 Fuel gas booster compressor | 49 | 66 | Full coverage
Fuel Oil | 13. Fuel Oil System | 13. Fuel Oil System | 25 | 1 | Full coverage; 24 row(s) below S>=3 threshold excluded.
Generator H2 | 35. STG NODE 10 H2 Cooler Vent & Drain,36. STG NODE 11 H2 - CO2 Control System | 35. STG NODE 10 H2 Cooler Vent & Drain | 8 | 8 | Full coverage
HP Steam | 1. HP steam System | 1. HP steam System | 15 | 10 | Full coverage; 5 row(s) below S>=3 threshold excluded.
HRH Steam | 3. Hot Reheat (HRH) Steam System | 3. Hot Reheat (HRH) Steam System | 14 | 9 | Full coverage; 5 row(s) below S>=3 threshold excluded.
HRSG Bypass | 21. HRSG NODE 09 By pass System GTG 7HA.03 and Casing System | 21. HRSG NODE 09 By pass System GTG 7HA.03 and Casing System | 13 | 6 | Full coverage; 7 row(s) below S>=3 threshold excluded.
HRSG Duct Burner | 23. HRSG NODE 07 Duct Burner TYPICAL (for HRSG 11, 12 and 13) | 23. HRSG NODE 07 Duct Burner TYPICAL (for HRSG 11, 12 and 13) | 27 | 6 | Full coverage; 21 row(s) below S>=3 threshold excluded.
HRSG HP | 17. HRSG NODE 01 H.P SECTION - TYPICAL (for HRSG 11, 12 and 13) | 17. HRSG NODE 01 H.P SECTION - TYPICAL (for HRSG 11, 12 and 13) | 29 | 20 | Full coverage; 9 row(s) below S>=3 threshold excluded.
HRSG IP | 18. HRSG NODE 02 IP STEAM TYPICAL (for HRSG 11, 12 and 13) | 18. HRSG NODE 02 IP STEAM TYPICAL (for HRSG 11, 12 and 13) | 33 | 19 | Full coverage; 14 row(s) below S>=3 threshold excluded.
HRSG LP | 19. HRSG NODE 03 LP STEAM TYPICAL (for HRSG 11, 12 and 13) | 19. HRSG NODE 03 LP STEAM TYPICAL (for HRSG 11, 12 and 13) | 38 | 21 | Full coverage; 17 row(s) below S>=3 threshold excluded.
LP Steam | 4. LP Steam System | 4. LP Steam System | 14 | 8 | Full coverage; 6 row(s) below S>=3 threshold excluded.
STG Lube Oil | 34. STG NODE 9 Lube Oil System | 34. STG NODE 9 Lube Oil System | 16 | 10 | Full coverage; 6 row(s) below S>=3 threshold excluded.
STG Seals | 30. STG NODE 5 Turbine Sealing System with Gland Condenser,38. STG NODE 13 Generator Shaft Seal System | 30. STG NODE 5 Turbine Sealing System with Gland Condenser | 18 | 19 | Full coverage
STG Steam | 26. STG NODE 1 By pass System GTG 7HA.03 and Casing System,27. STG NODE 2 Forced Air Cooling System,28. STG NODE 3 Steam System for HP Steam Turbine,29. STG NODE 4 Steam System for IP Steam & LP Steam Turbine,31. STG NODE 6 Turbine Steam Condensate Drain system | 26. STG NODE 1 By pass System GTG 7HA.03 and Casing System | 13 | 38 | Full coverage
(excluded) |  | 1. HP steam System | 5 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 10. Raw Water System | 31 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 11. CCCW system | 30 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 12. DM Water Distribution System | 42 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 13. Fuel Oil System | 24 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 14. Service Water System | 21 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 15. Potable Water system | 20 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 16. Industrial Gas System | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 17. HRSG NODE 01 H.P SECTION - TYPICAL (for HRSG 11, 12 and 13) | 9 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 18. HRSG NODE 02 IP STEAM TYPICAL (for HRSG 11, 12 and 13) | 14 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 19. HRSG NODE 03 LP STEAM TYPICAL (for HRSG 11, 12 and 13) | 17 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 2. CRH Steam System | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 20. HRSG NODE 04 Blowdown system TYPICAL (for HRSG 11, 12 and 13) | 19 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 21. HRSG NODE 09 By pass System GTG 7HA.03 and Casing System | 7 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 22. HRSG NODE 06 Closed Cooling Water System TYPICAL (for HRSG 11, 12 and 13) | 9 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 23. HRSG NODE 07 Duct Burner TYPICAL (for HRSG 11, 12 and 13) | 21 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 24. HRSG NODE 08 Ammonia unloading system TYPICAL (for HRSG 11, 12 and 13) | 11 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 25. HRSG NODE 09 Ammonia Consumption system TYPICAL (for HRSG 11, 12 and 13) | 25 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 26. STG NODE 1 By pass System GTG 7HA.03 and Casing System | 7 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 27. STG NODE 2 Forced Air Cooling System | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 28. STG NODE 3 Steam System for HP Steam Turbine | 7 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 29. STG NODE 4 Steam System for IP Steam & LP Steam Turbine | 7 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 3. Hot Reheat (HRH) Steam System | 5 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 30. STG NODE 5 Turbine Sealing System with Gland Condenser | 7 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 31. STG NODE 6 Turbine Steam Condensate Drain system | 14 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 32. STG NODE 7 Instrument Air System for STG | 5 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 33. STG NODE 8 Jacking Oil System | 17 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 34. STG NODE 9 Lube Oil System | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 35. STG NODE 10 H2 Cooler Vent & Drain | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 36. STG NODE 11 H2 - CO2 Control System | 13 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 37. STG NODE 12 Stator Winding Liquid Cooling System | 9 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 38. STG NODE 13 Generator Shaft Seal System | 10 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 39. FGS NODE 1 Fuel gas booster compressor | 35 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 4. LP Steam System | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 40. FGS NODE 2 Seal gas system for fuel gas booster compressor | 18 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 41. FGS NODE 3 Lubricating oil system for fuel gas booster compressor | 26 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 42. FGS NODE 4 Emergency shutdown valve (ESDV) skid, Settlement metering & back up metering skid, Conditioning skid and Pressure reducing skid | 7 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 43. FGS NODE 5 Dedicated pressure reducing station (PRCS) skid for GT #14 including startup and common heater skid | 12 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 44. FGS NODE 6 Pressure reducing station (PRCS) skid for HRSG & AUX. Boiler | 12 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 45. FGS NODE 7 IP performance heater skid for GT # 11, 12 & 13 along with startup and common heater skid | 10 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 46. FGS NODE 8 HP performance heater skid for GT # 11, 12 & 13 (TYPICAL) | 7 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 47. FGS NODE 9 Cold vent stack along with collection system | 2 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 48. FGS NODE 10 Common condensate tank for fuel gas conditioning area (NET capacity: 5 M3) | 15 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 49. FGS NODE 11 Individual block condensate tank for GT#11, 12, 13 & 14 area (Each NET capacity: 2 M3) | 31 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 5. Auxiliary steam system | 24 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 50. FGS NODE 12 Feed water from IP economizer outlet | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 51. FGS NODE 13 Water from HP economizer outlet | 9 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 52. FGS NODE 14 Fuel gas pressure regulating skid for water bath heater | 20 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 53. FGS NODE 15 Water bath heater | 8 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 54. FGS NODE 16 N2 Gas cylinder bank and supply system | 9 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 55. FGS NODE 17 Instrument air supply and distribution system | 5 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 56. ACC NODE 1 Steam & Condensate Collection System | 13 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 57. ACC NODE 2 Vacuum System | 17 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 58. ACC NODE 3 Fins Cleaning System | 14 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 6. Steam Vents & Drain System near STG | 18 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 7. Steam Vents & Drain System near HRSG | 19 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 8. Feed water system (TYPICAL) | 6 | 0 | No S>=3 rows / covered by parent system
(excluded) |  | 9. Condensate System | 46 | 0 | No S>=3 rows / covered by parent system

## Audit Log
Element ID | Finding | Severity | Original | Corrected | Rationale
PB-AC-019 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-AC-018 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-AC-017 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-AC-016 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-AC-015 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-AC-014 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-AC-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-AC-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-AC-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-AC-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-AC-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-AX-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-AX-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-AX-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-AX-001 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SL-006-X-AX | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SL-005-X-AX | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-AX-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-AX-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-AX-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-AX-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-AX-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-BY-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-BY-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-BY-001 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-BY-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-BY-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-BY-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-BY-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-BY-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-DB-003 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-DB-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-DB-005 | category corrected | INFO | Hardware - Passive | Hardware - Active | TAG_PREFIX_TO_CATEGORY override F4
PB-DB-004 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-DB-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-DB-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-DB-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-DB-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-DB-007 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-DB-006 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-DB-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-DB-005 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-DB-004 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-FG-023 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-FG-042 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FG-040 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FG-039 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FG-028 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FG-024 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FG-029 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FG-037 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FG-033 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FG-032 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FG-041 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FG-038 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FG-036 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FG-035 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FG-034 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FG-031 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-FG-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-FG-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-FG-003 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-FG-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-FG-008 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-FG-006 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-FG-005 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-FO-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-FO-006 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-FO-007 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-FO-004 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-FO-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-FO-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-FO-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FW-008 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-FW-007 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FW-006 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FW-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FW-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FW-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FW-009 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-FW-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-FW-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-FW-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-FW-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-FW-001 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-FW-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
PB-GH-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-GH-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-GH-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-GH-005 | category assigned (fallback) | INFO | fallback | Hardware - Passive | fallback (HW-Active default)
PB-GH-004 | category assigned (fallback) | INFO | fallback | Hardware - Passive | fallback (HW-Active default)
MB-GH-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-GH-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-GH-005 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-GH-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-GH-004 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-HI-012 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-HI-015 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HI-013 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HI-014 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HI-011 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HI-010 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HI-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-HI-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HI-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-HI-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-HI-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HL-013 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-HL-017 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HL-015 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HL-016 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HL-014 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HL-011 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HL-009 | category assigned (fallback) | INFO | fallback | Hardware - Passive | fallback (HW-Active default)
PB-HL-012 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-HL-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-HL-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HL-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-HL-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-HL-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HP-010 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HP-009 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HP-006 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HP-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HP-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HP-003 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HP-007 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-HP-008 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-HP-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HP-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-HP-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HP-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-HP-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-HP-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HR-015 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-HR-018 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HR-017 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HR-014 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HR-012 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HR-011 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HR-016 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HR-013 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HR-009 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HR-008 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HR-007 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HR-005 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-HR-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-HR-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HR-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-HR-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-HR-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-LP-006 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-LP-008 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-LP-007 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-LP-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-LP-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-LP-001 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-LP-003 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-LP-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-LP-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-LP-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-LP-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-LP-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-LP-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-NH-001 | category assigned (keyword) | INFO | keyword | Human - Active | FIX-02 keyword rules
PB-NH-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-NH-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-NH-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-NH-001 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-NH-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-NH-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-NH-006 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-NH-005 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-NH-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SS-004 | category assigned (keyword) | INFO | keyword | Human - Active | FIX-02 keyword rules
PB-SS-023 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SS-022 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SS-021 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SS-020 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SS-019 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SS-028 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SS-027 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SS-026 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SS-025 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SS-024 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SS-018 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-SS-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-SS-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-SS-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-SS-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
MB-SS-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-CR-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-CR-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-CR-001 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-AC-018-X-CD | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-CR-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-CR-001 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-CR-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
PB-HH-006 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
PB-HH-008 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-HH-007 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HH-003 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HH-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-HH-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HH-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-HH-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HH-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-HH-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HH-005 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-HH-004 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
MB-HH-002 | category assigned (keyword) | INFO | keyword | Organizational | FIX-02 keyword rules
PB-SL-014 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SL-013 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SL-012 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SL-011 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
PB-SL-010 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SL-009 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SL-004 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-SL-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-SL-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-SL-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-SL-003 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-SL-004 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-SL-005 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-LO-005 | category assigned (keyword) | INFO | keyword | Procedural | FIX-02 keyword rules
PB-LO-004 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-LO-003 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-LO-002 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
PB-LO-001 | category assigned (keyword) | INFO | keyword | Hardware - Active | FIX-02 keyword rules
MB-LO-001 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-LO-002 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-LO-004 | category assigned (fallback) | INFO | fallback | Hardware - Active | fallback (HW-Active default)
MB-LO-003 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
MB-LO-005 | category assigned (keyword) | INFO | keyword | Hardware - Passive | FIX-02 keyword rules
PB-CR-003 | barrier kept on source | INFO | CRH Steam | CRH/HRH Steam | PB kept-on-source (no live target): VALVE-10LBC01-AA402 from CRH Steam -> CRH/HRH Steam (P&ID prefix CR). HAZOP rows [91].
PB-CR-002 | barrier kept on source | INFO | CRH Steam | CRH/HRH Steam | PB kept-on-source (no live target): MOV-12LBC01-AA410 from CRH Steam -> CRH/HRH Steam (P&ID prefix CR). HAZOP rows [87].
PB-CR-001 | barrier kept on source | INFO | CRH Steam | CRH/HRH Steam | PB kept-on-source (no live target): MOV-11LBC01-AA001 from CRH Steam -> CRH/HRH Steam (P&ID prefix CR). HAZOP rows [80].
PB-LP-007 | barrier duplicated | INFO | LP Steam | HP Steam | PB duplicated: LABLE11LBA30-CT121 from LP Steam -> HP Steam (P&ID prefix HP). HAZOP rows [243].
PB-AX-002 | barrier kept on source | INFO | Auxiliary Steam | CRH/HRH Steam | PB kept-on-source (no live target): VALVE-10LBC10-AA406 from Auxiliary Steam -> CRH/HRH Steam (P&ID prefix CR). HAZOP rows [298].
PB-AX-001 | barrier kept on source | INFO | Auxiliary Steam | CRH/HRH Steam | PB kept-on-source (no live target): MOV-10LBC06-AA402 from Auxiliary Steam -> CRH/HRH Steam (P&ID prefix CR). HAZOP rows [289].
PB-HR-015 | barrier duplicated | INFO | HRSG HP | HP Steam | PB duplicated: NRV-11LBA10-AA201 from HRSG HP -> HP Steam (P&ID prefix HP). HAZOP rows [1235].
PB-HR-011 | barrier duplicated | INFO | HRSG HP | HP Steam | PB duplicated: MOV-11LBA10-AA102 from HRSG HP -> HP Steam (P&ID prefix HP). HAZOP rows [1210].
PB-HR-016 | barrier duplicated | INFO | HRSG HP | Feedwater | PB duplicated: VALVE-11LAB63-AA101 from HRSG HP -> Feedwater (P&ID prefix FW). HAZOP rows [1239].
PB-HR-009 | barrier duplicated | INFO | HRSG HP | Feedwater | PB duplicated: VALVE-11LAE10-AA102 from HRSG HP -> Feedwater (P&ID prefix FW). HAZOP rows [1199].
PB-HR-008 | barrier duplicated | INFO | HRSG HP | Feedwater | PB duplicated: PDAH-11LAE40-CF181 from HRSG HP -> Feedwater (P&ID prefix FW). HAZOP rows [1189].
PB-HR-007 | barrier duplicated | INFO | HRSG HP | Feedwater | PB duplicated: VALVE-11LAE10-AA104 from HRSG HP -> Feedwater (P&ID prefix FW). HAZOP rows [1181].
PB-HR-005 | barrier duplicated | INFO | HRSG HP | Feedwater | PB duplicated: PDAH-11LAE10-CP181 from HRSG HP -> Feedwater (P&ID prefix FW). HAZOP rows [1169].
PB-HI-012 | barrier duplicated | INFO | HRSG IP | HP Steam | PB duplicated: NRV-11LBA20-AA201 from HRSG IP -> HP Steam (P&ID prefix HP). HAZOP rows [1390].
PB-HI-011 | barrier duplicated | INFO | HRSG IP | HRSG HP | PB duplicated: LAH-11HAD20-CL121 from HRSG IP -> HRSG HP (P&ID prefix HR). HAZOP rows [1381].
PB-HL-013 | barrier cross-referenced | INFO | HRSG LP | HP Steam | PB cross-ref (target already carried tag): NRV-11LBA10-AA201 from HRSG LP -> HP Steam (P&ID prefix HP). HAZOP rows [1548].
PB-HL-016 | barrier duplicated | INFO | HRSG LP | Feedwater | PB duplicated: VALVE-11LAB61-AA102 from HRSG LP -> Feedwater (P&ID prefix FW). HAZOP rows [1564].
PB-HL-014 | barrier cross-referenced | INFO | HRSG LP | Feedwater | PB cross-ref (target already carried tag): VALVE-11LAB63-AA101 from HRSG LP -> Feedwater (P&ID prefix FW). HAZOP rows [1554].
PB-HL-011 | barrier duplicated | INFO | HRSG LP | HRSG HP | PB duplicated: PAH-11HAD30-CP121 from HRSG LP -> HRSG HP (P&ID prefix HR). HAZOP rows [1543].
PB-HL-009 | barrier duplicated | INFO | HRSG LP | HP Steam | PB duplicated: PSV-11LBA30-AA191 from HRSG LP -> HP Steam (P&ID prefix HP). HAZOP rows [1526].
PB-HL-012 | barrier cross-referenced | INFO | HRSG LP | HRSG HP | PB cross-ref (target already carried tag): PAH-11HAD30-CP121 from HRSG LP -> HRSG HP (P&ID prefix HR). HAZOP rows [1543].
PB-SS-022 | barrier duplicated | INFO | STG Steam | LP Steam | PB duplicated: PCV-10LCE81-AA001 from STG Steam -> LP Steam (P&ID prefix LP). HAZOP rows [2100].
PB-SS-021 | barrier duplicated | INFO | STG Steam | LP Steam | PB duplicated: PDAH-10LCE81-CP122 from STG Steam -> LP Steam (P&ID prefix LP). HAZOP rows [2094].
PB-SS-020 | barrier duplicated | INFO | STG Steam | ACC | PB duplicated: TAH-10MAC81-CT053A/B from STG Steam -> ACC (P&ID prefix AC). HAZOP rows [2089].
PB-SL-012 | barrier cross-referenced | INFO | STG Seals | Generator H2 | PB cross-ref (target already carried tag): PSL10MKG21-CP101 from STG Seals -> Generator H2 (P&ID prefix GH). HAZOP rows [2513].
PB-SL-006 | barrier duplicated | INFO | STG Seals | Auxiliary Steam | PB duplicated: TAH-10MAW82-CT055 from STG Seals -> Auxiliary Steam (P&ID prefix AX). HAZOP rows [2186].
PB-SL-005 | barrier duplicated | INFO | STG Seals | Auxiliary Steam | PB duplicated: TAL-10MAW82-CT055 from STG Seals -> Auxiliary Steam (P&ID prefix AX). HAZOP rows [2178].
PB-SL-003 | barrier duplicated | INFO | STG Seals | Auxiliary Steam | PB duplicated: PAH-10MAW84-CP129 from STG Seals -> Auxiliary Steam (P&ID prefix AX). HAZOP rows [2145].
PB-SL-001 | barrier duplicated | INFO | STG Seals | Auxiliary Steam | PB duplicated: PAL-10MAW81-CP121 from STG Seals -> Auxiliary Steam (P&ID prefix AX). HAZOP rows [2120].
PB-GH-001 | barrier kept on source | INFO | Generator H2 | CCCW | PB kept-on-source (no live target): PAL-00PGB07-CP101A/B from Generator H2 -> CCCW (P&ID prefix CW). HAZOP rows [2362].
PB-AC-018 | barrier duplicated | INFO | ACC | Condensate | PB duplicated: FAL-10LCA04-CF101A/B from ACC -> Condensate (P&ID prefix CD). HAZOP rows [3623].
PB-AC-016 | barrier duplicated | INFO | ACC | Auxiliary Steam | PB duplicated: MOV-10LBG45-AA080 from ACC -> Auxiliary Steam (P&ID prefix AX). HAZOP rows [3606].
PB-AC-015 | barrier duplicated | INFO | ACC | Auxiliary Steam | PB duplicated: PAL-10LBG45-CP001 from ACC -> Auxiliary Steam (P&ID prefix AX). HAZOP rows [3595].